## Title
Title: | SmartValve 10-1800 v1.04 - HV-ISO-XFMR Board Rev3 (P112469) - Failure Mode Effects and Criticality Analysis (Design FMECA)
Project: | SmartValve 10-1800 v1.04
PS19 QPI | PS19 Technical Experts | Smart Wires Reviewer
Azeem, Talha, Adeel, Ashad | Abdul Qadeer, Abdul Rehman | Susie Choi

## Revision History
Revision History
Date | Version | Description
2021-01-19 | 1 | Initial draft based on HVT Board FMECA Rev0 by PS19 QPI Team
2021-03-04 | 1.1 | Updated based on HVT Board FMECA Rev1 by PS19 QPI Team
2022-01-21 | 1.2 | Updated based on HVT Board FMECA Rev2 by PS19 QPI Team
2022-02-02 | 1.3 | Reviewed by PS19 Hardware team for the changes done based on the Rev2 schematic
2022-02-07 | 1.4 | Updated by PS19 QPI team based on the feedback by PS19 Harware Team on Rev2 schematic
2022-03-18 | 1.5 | Reveiwed and updated by DR. Susie based on the Rev2 schematic
2022-07-29 | 1.6 | Updated based on HVT Board FMECA Rev3 by PS19 QPI Team
2022-08-01 | 1.7 | Reviewed by PS19 Hardware team for the changes done based on the Rev3 schematic
2022-09-20 | 1.8 | Updated by PS19 QPI team based on the feedback by PS19 Smart Wires Team on Rev3 schematic
2022-09-28 | 1.9 | Reviewed by PS19 Hardware team for the changes done based on the Rev3 schematic
2022-10-06 | 2 | Updated by PS19 QPI team based on feedback from Smart Wires and PS19 Hardware Team
2022-10-14 | 2.1 | Reviewed by PS19 Hardware team for the changes done based on the Rev3 schematic
2022-10-19 | 2.2 | Updated by PS19 QPI team based on feedback from Smart Wires and PS19 Hardware Team
2022-11-18 | 2.3 | Updated by PS19 QPI team based on feedback from Smart Wires Team

## Definitions-Terms
Definitions / Terms / Acronyms
Term | Description | Term | Description
A-K | Anode-to-Cathode | LCB | Liquid Cooling Block
BF | Bypass Filter | PHT | Power Harvesting Transformer
CTP | Current Transformer for Power | ETP | Electrical Test Procedure
DCCT | DC current transducer | IP | Intrusion Protection
DCE | Digital Computational Engine | MES | Manufacturing Execution System
EFT | Electrical Fast Transient | CTQ | Critical To Quality
EMS | Energy Management System
EOL | End Of Line
FCS | Fault Current Sensor
FO | Fiber Optic
FR | Flame Retardant
G-K | Gate-to-Cathode
HALT | Highly-Accelerated Life Testing
HASS | High accelerated stress screening
HCT | High Current Testing
LCB | Liquid Cooling Block
LCS | Line Current Sensor
OVP | Over-Voltage Protection
PCB | Printed Circuit Board
PIB | Power Interface Board
PLM | PowerLine Manager
PSB | Power Supply Board
RF | Radio Frequency
RTU | Remote Terminal Unit
SB | Smart Bypass
SCR | Silicon Controlled Rectifier
SI | Smart Interface
SMD | Surface Mounted Device
SV | Smart Valve
SVC | SmartValve Controller
VPI | Vacuum Pressure Impregnation
VSL | Vacuum Series Link
UPSB | Universal Power Supply Board
TBR | To be Reviewed

## Scores
|  | Risk Factor (S x O) Scores | [5 empty] | SmartValve v1.04 Risk Factor (S x O) Counts
Occurrence | 5 | 5 | 10 | 15 | 20 | 25 | Occurrence | 5 | 0 | 0 | 0 | 0 | 0
| 4 | 4 | 8 | 12 | 16 | 20 |  | 4 | 0 | 0 | 0 | 0 | 0
| 3 | 3 | 6 | 9 | 12 | 15 |  | 3 | 0 | 0 | 0 | 0 | 0
| 2 | 2 | 4 | 6 | 8 | 10 |  | 2 | 25 | 47 | 8 | 4 | 0
| 1 | 1 | 2 | 3 | 4 | 5 |  | 1 | 310 | 422 | 77 | 94 | 6
|  | 1 | 2 | 3 | 4 | 5 |  |  | 1 | 2 | 3 | 4 | 5
|  | Severity | [6 empty] | Severity
[9 empty] | Total risks: |  |  |  | 993
[9 empty] | Total risks require mitigation based on S x O: |  |  |  | 10
| Risk Priority Number (S x O x D) Scores | [6 empty] | SmartValve v1.04 RPN (S x O x D) Counts
Severity x Occurrence (S x O) | 25 | 25 | 50 | 75 | 100 | 125 | Severity x Occurrence (S x O) | 25 | 0 | 0 | 0 | 0 | 0
| 24 | 24 | 48 | 72 | 96 | 120 |  | 24 | 0 | 0 | 0 | 0 | 0
| 23 | 23 | 46 | 69 | 92 | 115 |  | 23 | 0 | 0 | 0 | 0 | 0
| 22 | 22 | 44 | 66 | 88 | 110 |  | 22 | 0 | 0 | 0 | 0 | 0
| 21 | 21 | 42 | 63 | 84 | 105 |  | 21 | 0 | 0 | 0 | 0 | 0
| 20 | 20 | 40 | 60 | 80 | 100 |  | 20 | 0 | 0 | 0 | 0 | 0
| 19 | 19 | 38 | 57 | 76 | 95 |  | 19 | 0 | 0 | 0 | 0 | 0
| 18 | 18 | 36 | 54 | 72 | 90 |  | 18 | 0 | 0 | 0 | 0 | 0
| 17 | 17 | 34 | 51 | 68 | 85 |  | 17 | 0 | 0 | 0 | 0 | 0
| 16 | 16 | 32 | 48 | 64 | 80 |  | 16 | 0 | 0 | 0 | 0 | 0
| 15 | 15 | 30 | 45 | 60 | 75 |  | 15 | 0 | 0 | 0 | 0 | 0
| 14 | 14 | 28 | 42 | 56 | 70 |  | 14 | 0 | 0 | 0 | 0 | 0
| 13 | 13 | 26 | 39 | 52 | 65 |  | 13 | 0 | 0 | 0 | 0 | 0
| 12 | 12 | 24 | 36 | 48 | 60 |  | 12 | 0 | 0 | 0 | 0 | 0
| 11 | 11 | 22 | 33 | 44 | 55 |  | 11 | 0 | 0 | 0 | 0 | 0
| 10 | 10 | 20 | 30 | 40 | 50 |  | 10 | 0 | 0 | 0 | 0 | 0
| 9 | 9 | 18 | 27 | 36 | 45 |  | 9 | 0 | 0 | 0 | 0 | 0
| 8 | 8 | 16 | 24 | 32 | 40 |  | 8 | 0 | 3 | 0 | 0 | 0
| 7 | 7 | 14 | 21 | 28 | 35 |  | 7 | 0 | 0 | 0 | 0 | 0
| 6 | 6 | 12 | 18 | 24 | 30 |  | 6 | 0 | 0 | 0 | 0 | 8
| 5 | 5 | 10 | 15 | 20 | 25 |  | 5 | 1 | 0 | 0 | 0 | 5
| 4 | 4 | 8 | 12 | 16 | 20 |  | 4 | 10 | 96 | 0 | 0 | 36
| 3 | 3 | 6 | 9 | 12 | 15 |  | 3 | 0 | 0 | 0 | 0 | 77
| 2 | 2 | 4 | 6 | 8 | 10 |  | 2 | 79 | 76 | 0 | 0 | 292
| 1 | 1 | 2 | 3 | 4 | 5 |  | 1 | 1 | 1 | 0 | 0 | 308
|  | 1 | 2 | 3 | 4 | 5 |  |  | 1 | 2 | 3 | 4 | 5
|  | Detection | [6 empty] | Detection
[8 empty] | Total risks: |  |  |  |  | 993
[8 empty] | Total risks require mitigation based on S x O x D: |  |  |  |  | 0

## S-O-D Definitions
Severity, or Consequence Evaluation Criteria: Worst Case Evaluation of Failure Mode |  |  |  | Occurrence: Probability of occurrence within the product life based on the design as is exists today
Score | Criteria | Notes | Example | Score | Notes | Probability Description | Probability
5 | Failure causes death or causes transmission line open circuit, full or partial fault protection compromised. | Extremely hazardous failure, threatening to business continuity. | Fault detection mechanism failure . IGBT shorting the capacitor bank. Power to one or more SCR driver boards discontinued while unit is in injection mode. Mechanical failure causing line to open. | 5 | Very high probability | 1 in 10 or greater | 0.1 ≤ Po
4 | Failure causes severe injury to personnel requiring hospitalization, severe property damage such as damage to a structure, transmission line damage, major damage to system other than transmission line requiring immediate interruption of line service, loss of control of SmartValve v1.04 when in Injection Mode, device is forced to monitoring mode, with reduced fault protection (i.e. redundancy compromised). | Highly hazardous failure, threatening to business reputation. | iiDCE RF communication loss in injection mode. iiDCE losing control of SCRs. | 4 | High probability | 1 in 100 or greater | 0.01 ≤ Po < 0.1
3 | Failure causes minor injury to personnel requiring out-patient treatment, moderate property damage not involving a structure, moderate system damage other than transmission line that requires future interruption of line service to repair, loss of control of SmartValve v1.04 when in Monitoring Mode, device is forced to monitoring mode with full fault protection available. | Moderately hazardous failure, threatening to product reputation. | iiDCE RF communication loss in monitoring mode. Any control boards' failure, forcing device to monitoring mode. Mechanical failure causing enclosure temperature to rise, forcing device to stay in monitoring mode. | 3 | Moderate probability | 1 in 1,000 or greater | 0.001 ≤ Po < 0.01
2 | Failure causes minor property damage, minor system damage other than primary conductor or loss of SmartValve v1.04 such as loss of performance, unit forced into Monitoring Mode, or significant impact on unit life | Minor hazard, minor consequence. | Rise in on-board power losses, impacting components' life, Clamp board feedback not available. | 2 | Low probability | 1 in 10,000 or greater | 0.0001 ≤ Po < 0.001
1 | Failure causes unscheduled maintenance, no immediate loss of performance. | No hazard. | On-board noise filtration compromised. One of many bolts failure. | 1 | Remote probability | Less than 1 in 10,000 | Po < 0.0001
Detection: Likelihood of failure mode detection by design | [5 empty] | Target product life for the purposes of this FMECA is 40 years.
Score | Description | Criteria | Definition
5 | Very remote probability to absolute uncertainty of detection | Design will not and/or cannot detect the potential cause/mechanism or subsequent failure mode, or the likelihood of detection is very remote. | PD < 0.1 | RPN Conditions | Color
4 | Very low to remote probability of detection | Design has a very low to remote likelihood of detecting the potential cause/mechanism or subsequent failure mode. | 0.1 ≤ PD < 0.5 | Value ≥ 70
3 | Moderate to low probability of detection | Design has a moderate to low likelihood of detecting the potential cause/mechanism or subsequent failure mode. | 0.5 ≤ PD < 0.95 | 70 > Value ≥ 60
2 | High to moderately high probability of detection | Design has a high to moderately high likelihood of detecting the potential cause/mechanism or subsequent failure mode. | 0.95 ≤ PD < 0.995 | 60 > Value ≥ 50
1 | Almost certain to very high probability of detection | Design has an almost certain chance of detecting the potential cause/mechanism or subsequent failure mode or the likelihood of detection is very high. | 0.995 ≤ PD | Value < 50
Review Status
Approved
Reviewed by QA
Review Pending

## Design-Traceability
Design Traceability
Sr. | Design Artifact | Rev | Link
1 | SmartValve 10-1800 v1.04 - Wiring Drawing - Bypass Section Harnesses Diagram | 2 | Box Link
2 | SmartValve 10-1800 v1.04 - Wiring Drawing - MVAR Section Harnesses Diagram | 2 | Box Link
3 | SmartValve 10-1800 v1.04 - Wiring Drawing - PHT Shorting and Capacitor Voltage Measurement Blocks | 2 | Box Link
4 | SmartValve 10-1800 v1.04 - Wiring Drawing - Power Supply Scheme Gen2-v2-FAI | 2 | Box Link
5 | SmartValve 10-1800 v1.04 - PCBAs - HV-ISO XFMR Board Functional Block Diagram | 3 | Box Link
6 | SmartValve 10-1800 v1.04 - PCBAs - HV-ISO XFMR Board Schematic | 3 | Box Link
7 | SmartValve 10-1800 v1.04 - PCBAs - HV-ISO XFMR Board Design Document | A | Box Link

## DFMECA
ID. | Component | Reference Designator | Functional Requirement | Potential Failure Mode | Potential Effect(s) of Failure |  |  | Severity Score | Potential Causes / Triggers of Failure | Failure Safeguards | Occurrence Score | S x O | Existing Conditions |  |  | RPN (S x O x D) | Alert Message | Alert Message | Recommended Action(s) / Remarks | Reporting Team Member | Target Completion Date | Action Results |  |  |  |  | Status
[5 empty] | Local - Effect at the sub assembly or component level | Higher Level - Effect at SmartValve v1.04 | End - Effect at System Level | [5 empty] | Verification & Validation Method | Detection Method | Detection Score | [6 empty] | Actions Taken | Severity Score | Occurrence Score | Detection Score | New RPN
| HV Transformer Board Rev3 (P112469) | [26 empty] | 0
| HV Transformer Board for one iSCR Driver Board | [26 empty] | 0
| 15 V On-Board Supply | [26 empty] | 0
SV104-10917 | Input Side Connector | J3 | Input supply from PHTDC | Connector Disconnected by external Force. | Input power path will be broken. No output available at HV transformer board. | iSCR driver board will still receive power from redundant HVT board. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Open Connections due to vibrations, mis-handling or mechanical stress. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iSCR driver board. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. Vibration Testing. | None. | 5 | 10 | [9 empty] | 0 |  | 10917
SV104-10918 |  |  |  | Connection Loose or Sparking at terminals | Due to sparking connector will heat up and eventually burnout | iSCR driver board will still receive power from redundant HVT board. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Open Connections due to vibrations, mis-handling or mechanical stress. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iSCR driver board. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. Vibration Testing. | None. | 5 | 10 | [9 empty] | 0 |  | 10918
SV104 - 5158 | Input Side TRIACs. | D13,D12 | Reverse polarity protection. | TRIAC fails-open. | No immediate effect. Board will keep working, but it is going to increase some level of stress on other components which will have an impact in longer run(Years). Board life is going to be impacted. Parallel TRIAC available for alternate path. | If no other failure is observed on the board, iSCR driver board will stay powered. Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | Excessive forward current. Open Connections due to vibrations, mis-handling or mechanical stress. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iSCR driver board. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. Vibration Testing. | None. | 5 | 5 | [9 empty] | 0 |  | 5158
SV104 - 5159 |  |  |  | TRIAC fails-short. | Reverse polarity protection will be compromised during shortage. Board will keep working normally if input is provided with correct polarity. | If no other failure is observed on the board, iSCR driver board will stay powered. Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | Large reverse voltage. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iSCR driver board. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [11 empty] | 5159
SV104 - 6736 |  |  |  | Both TRIACs fail-short. | Reverse polarity protection will be compromised. Board will keep working normally if input is provided with correct polarity. | If no other failure is observed on the board, iSCR driver board will stay powered. Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | Large reverse voltage. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iSCR driver board. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [11 empty] | 6736
SV104 - 6737 |  |  |  | Both TRIACs fail-open | Input path will be broken. No output available at HV transformer board. . | iSCR driver board will still receive power from redundant HVT board. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Excessive forward current. Open Connections due to vibrations, mis-handling or mechanical stress. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iSCR driver board. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. Vibration Testing. | None. | 5 | 10 | [11 empty] | 6737
SV104 - 5160 | Input Side Fuse. | F2 | To cut-off supply in case of over-current. | Fuse fails-open. | Input power path will be broken. No output available at HV transformer board. | iSCR driver board will still receive power from redundant HVT board. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | On-board fault causing higher current flow. De-gradation of components. Open Connections due to vibrations, mis-handling or mechanical stress. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iSCR driver board. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. Vibration Testing. | None. | 5 | 10 | [9 empty] | 0 |  | 5160
SV104 - 5161 | Input Side Filter Capacitors. | C2,C23 | To suppress ripples on input voltage. | Capacitor fails-open. | Input supply ripples may cause distorted output supply. No immediate effect on board.. | If no other failure is observed on the board, iSCR driver board will stay powered. Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | Mechanical stress. Localized heating for long time will separate end connection of capacitor. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iSCR driver board. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. Vibration Testing. | None. | 5 | 5 | [9 empty] | 0 |  | 5161
SV104 - 5162 |  |  |  | Capacitor fails-short. | PHT-DC Capacitor will dump full energy in HV-ISO board leaving it permanently damage (Trace damage). No output available at HV transformer board. | iSCR driver board will still receive power from redundant HVT board. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Wear-out due to dielectric degradation. High-voltage transients. De-gradation of components. Water ingress during humidity condition as it is film capacitor. Overvoltage | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. RTV application on edges to stop water ingress. Redundant HV Transformer board to power-up iSCR driver board. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. Environmental Testing. | None. | 5 | 10 | [11 empty] | 5162
SV104 - 5163 | Low Voltage Detection Zener Diode. (D7, D11, D10) | D7,D10,D11 | To set under-voltage lockout threshold. | Diode fails-open. | No voltage will be available at power controlling MOSFET gate. On-board 15 V supply will not be available. No output available at HV transformer board. | iSCR driver board will still receive power from redundant HVT board. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Mechanical stress or impact during assembly. Overcurrent. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iSCR driver board. | 2 | 4 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 20 | [9 empty] | 0 |  | 5163
SV104 - 5164 |  |  |  | Diode fails-short.. | The threshold for UVLO detection will decrease. Board will turn on before the set threshold of 320 V. Slight effect will be on PHT-DC bus during low line current condition as it will ramp up slowly. Board will keep working. | If no other failure is observed on the board, iSCR driver board will stay powered. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Excessive Temperature. High reverse voltage. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iSCR driver board. | 2 | 4 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 20 | [11 empty] | 5164
SV104-10919 | Low Voltage Detection Voltage Divider | R41,R36 | To set UVLO threshold | Resistor fails-open. | No voltage will be available at power controlling MOSFET gate. On-board 15 V supply will not be available. No output available at HV transformer board. | iSCR driver board will still receive power from redundant HVT board. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Over voltage. Over Temperature. Over stress due to shock or vibration. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iSCR driver board. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. Vibration testing. | None. | 5 | 10 | [11 empty] | 10919
SV104-10920 |  |  |  | Resistor fails-short. | UVLO limit will decrease ,no major effect. Board will powerup at few volts lesser voltage. Board will keep working. | If no other failure is observed on the board, iSCR driver board will stay powered. Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | Wear-out due to extensive use. Excessive humidity. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iSCR driver board. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. Vibration testing. | None. | 5 | 5 | [11 empty] | 10920
SV104 - 5165 | Input Side Voltage Divider Resistor. | R30,R31,R32,R33,R34,R35 | To step down voltage. | Resistor fails-open. | No voltage will be available at power controlling MOSFET gate. On-board 15 V supply will not be available. No output available at HV transformer board. | iSCR driver board will still receive power from redundant HVT board. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Over Temperature. Over stress due to shock or vibration. De-gradation of components. Overcurrent. Counterfeit part. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iSCR driver board. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. Vibration testing. | None. | 5 | 10 | [11 empty] | 5165
SV104 - 5166 |  |  |  | Any one resistor fails-short. | No immediate effect on board. Board will keep working normally. | iSCR driver board will still receive power from redundant HVT board. Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | Wear-out due to extensive use. Excessive humidity. Counterfeit part. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Conformal coating. Redundant HV Transformer board to power-up iSCR driver board. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. Vibration testing. | None. | 5 | 5 | [11 empty] | 5166
SV104 - 12377 |  |  |  | More than one resistors fails-short. | Soft starting current is increased significantly consequently MOSFET power dissipation will increase that could bring failure. No output available at HV transformer board. | iSCR driver board will still receive power from redundant HVT board. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Wear-out due to extensive use. Excessive humidity. Counterfeit part. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements.. Conformal coating. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. Vibration testing. | None. | 5 | 10 | [11 empty] | 12377
SV104 - 5167 | Input Power Control MOSFET. | Q6 | To turn ON/OFF power flow. | MOSFET fails-open. | Input power path will be broken. No output available at HV transformer board. | iSCR driver board will still receive power from redundant HVT board. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Overheating Mechanical stress resulting in cracked MOSFET body. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iSCR driver board. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 10 | [9 empty] | 0 |  | 5167
SV104 - 5168 |  |  |  | MOSFET fails-short. | Startup circuitry will turn on permanently resulting in overheating and permanently damage to startup resistor. No output available once HV-ISO reboot. | iSCR driver board will still receive power from redundant HVT board. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Transients Overheating as a result of loose connection with heat sink Overcurrent Counterfeit part Damage during mechanical assembly of board Metallic debris stuck in between terminals | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iSCR driver board. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 10 | [11 empty] | 5168
SV104 - 5169 | Over-voltage Protection Zener Diode at MOSFET Gate Side. | D31 | For gate protection of MOSFET. | Diode fails-open. | Over-voltage protection of MOSFET won't be available. No immediate effect on board in normal operations. | If no other failure is observed on the board, iSCR driver board will stay powered. Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | Mechanical stress or impact during assembly. Overcurrent. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 2 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 10 | [9 empty] | 0 |  | 5169
SV104 - 5170 |  |  |  | Diode fails-short. | MOSFET will be turned off completely. Startup circuit will not work. No output available at HV transformer board. | iSCR driver board will still receive power from redundant HVT board. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Large reverse voltage. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 2 | 4 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 20 | [11 empty] | 5170
SV104-12378 | Filtration Capacitor | C21 | To suppress noise and remove ripples | Capacitor fails-open. | No immediate effect on board. Board will keep working normally. | If no other failure is observed on the board, iSCR driver board will stay powered. Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | Mechanical stress. Localized heating for long time will separate end connection of capacitor. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iSCR driver board. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. Vibration Testing. | None. | 5 | 5 | [11 empty] | 12378
SV104-12379 |  |  |  | Capacitor fails-short. | HVDC and 24VAUX will be shorted top ground. Startup circuit will not work. Input Fuse Will be Blown No output available at HV transformer board. | iSCR driver board will still receive power from redundant HVT board. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Wear-out due to dielectric degradation. High-voltage transients. De-gradation of components. Water ingress during humidity condition as it is film capacitor. Overvoltage | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. RTV application on edges to stop water ingress. Redundant HV Transformer board to power-up iSCR driver board. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. Environmental Testing. | None. | 5 | 10 | [11 empty] | 12379
SV104-10921 | MOSFET resistance for Miller Capacitance | R37 | To discharge miller capacitance of MOSFET | Resistor fails-open | Abnormal Behavior of MOSFET Might turn ON/OFF abnormally can damage startup circuitry if MOSFET remains on for longer duration. No output available at HV transformer board | iSCR driver board will still receive power from redundant HVT board. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Over voltage. Over Temperature. Over stress due to shock or vibration. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iSCR driver board. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. Vibration testing. | None. | 5 | 10 | [11 empty] | 10921
SV104-10922 |  |  |  | Resistor fails-short | Gate and Source of Q6 will have no voltage difference so MOSFET cannot operate No output available at HV transformer board | iSCR driver board will still receive power from redundant HVT board. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Wear-out due to extensive use. Excessive humidity. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iSCR driver board. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. Vibration testing. | None. | 5 | 10 | [11 empty] | 10922
SV104 - 6738 | D21-Free wheeling diode | D21 | To protect BJT during reverse voltage condition | Diode fails-open. | No protection for BJT will be available. Reverse voltage development across BJT will damage it. No output available. | iSCR driver board will still receive power from redundant HVT board. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Mechanical stress or impact during assembly. Overcurrent. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iSCR driver board. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 10 | [11 empty] | 6738
SV104 - 6739 |  |  |  | Diode fails-short. | Input will appear as it is on output which will damage PWM controller and gate driver ICs permanently. No output available. | iSCR driver board will still receive power from redundant HVT board. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Large reverse voltage. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iSCR driver board. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 10 | [11 empty] | 6739
SV104 - 6740 | D22-To prevent reverse power flow | D22 | To prevent reverse power flow from auxiliary to startup circuitry | Diode fails-open. | Input power path will be broken. No output available at HV transformer board. | iSCR driver board will still receive power from redundant HVT board. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Mechanical stress or impact during assembly. Overcurrent. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iSCR driver board. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 10 | [11 empty] | 6740
SV104 - 6741 |  |  |  | Diode fails-short. | If the board is OFF than it can not turn ON. If board is ON than reverse power will start to flow. D31 will be forward biased and as gate of Q6 is grounded than 24VAUX will also be grounded. No output available at HV transformer board. | iSCR driver board will still receive power from redundant HVT board. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Large reverse voltage. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iSCR driver board. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 10 | [11 empty] | 6741
SV104 - 6742 | D27-Zener diode | D27 | To set reference voltage for BJT to regulate | Diode fails-open. | Voltage at input will appear as it is on base damaging it permanently. No output available at HV transformer board. | iSCR driver board will still receive power from redundant HVT board. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Mechanical stress or impact during assembly. Overcurrent. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iSCR driver board. | 2 | 4 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 20 | [11 empty] | 6742
SV104 - 6743 |  |  |  | Diode fails-short. | BJT will not turn on. No output available at HV transformer board. | iSCR driver board will still receive power from redundant HVT board. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Large reverse voltage. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iSCR driver board. | 2 | 4 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 20 | [11 empty] | 6743
SV104 - 5171 | Input Power Control BJT. | Q8 | To provide regulated voltage for startup. | BJT fails-open. | Input power path will be broken. No output available at HV transformer board. | iSCR driver board will still receive power from redundant HVT board. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Melted connections due to overheating. Manufacturing defect. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iSCR driver board. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 10 | [9 empty] | 0 |  | 5171
SV104 - 5172 |  |  |  | BJT fails-short. | Higher voltage at startup will damage the PWM controller and gate drivers of board. Input power path will be broken. No output available at HV transformer board. | iSCR driver board will still receive power from redundant HVT board. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Over voltage. Leaky junctions. Wear-out due to high power dissipation. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iSCR driver board. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 10 | [11 empty] | 5172
SV104 - 5173 | Biasing Resistor for BJT. | R40 | To set biasing threshold for power flow controlling BJT. | Resistor fails-open. | BJT will be permanently turned OFF. Input power path will be broken. No output available at HV transformer board. | iSCR driver board will still receive power from redundant HVT board. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Over voltage. Over Temperature. Over stress due to shock or vibration. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iSCR driver board. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 10 | [9 empty] | 0 |  | 5173
SV104 - 5174 |  |  |  | Resistor fails-short. | 24 V will be replicated at the emitter for the shorted duration, on-board ICs may get burn due to this over-voltage. BJT will eventually fail-open due to over-current. Input power path will be broken. No output available at HV transformer board. | iSCR driver board will still receive power from redundant HVT board. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Wear-out due to extensive use. Excessive humidity. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iSCR driver board. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 10 | [11 empty] | 5174
SV104 - 5175 | Freewheeling Diode. |  | To provide reverser current flow path. | Diode fails-open. | No path will be available for reverse current to flow. Potential difference creation across BJT can damage the BJT. Input power path will be broken. No output available at HV transformer board. | iSCR driver board will still receive power from redundant HVT board. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Mechanical stress or impact during assembly. Overcurrent. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iSCR driver board. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 10 | [11 empty] | 5175
SV104 - 5176 |  |  |  | Diode fails-short. | An emitter to collector short on BJT will cause the BJT to over-heat and may fail-open. Input power path will be broken. No output available at HV transformer board. | iSCR driver board will still receive power from redundant HVT board. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Large reverse voltage. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iSCR driver board. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 10 | [11 empty] | 5176
SV104 - 5177 | 15 V Rail Output Side Capacitors. | C22,C19,C20 | To stable output voltage and to suppress ripples. | Capacitor fails-open. | No immediate effect on board.. | If no other failure is observed on the board, iSCR driver board will stay powered. Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | Mechanical stress. Localized heating for long time will separate end connection of capacitor. | Using enough filtration capacitors at different levels. Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [9 empty] | 0 |  | 5177
SV104 - 5178 |  |  |  | Capacitor fails-short. | 15 V power supply will be shorted to ground. On-board electronics will not be powered up. No output available at HV transformer board. | iSCR driver board will still receive power from redundant HVT board. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Wear-out due to dielectric degradation. High-voltage transients. De-gradation of components. | Using enough filtration capacitors at different levels. Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 10 | [11 empty] | 5178
SV104 - 5179 | 24 V Feedback Signal Side Resistor. | R38 | To provide 24 V sensing feedback path. | Resistor fails-open. | 15 V regulator will keep on working from input side and will not turn off. Which will heat up the resistor on MOSFET Q6 drain and will burn out eventually. No output available at HV transformer board. | iSCR driver board will still receive power from redundant HVT board. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Over voltage. Over Temperature. Over stress due to shock or vibration. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iSCR driver board. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 10 | [9 empty] | 0 |  | 5179
SV104 - 5180 |  |  |  | Resistor fails-short. | Over-current will cause the resistor to eventually fail-open. 15 V regulator will keep on working from input side and will not turn off. Which will heat up the resistor on MOSFET Q6 drain and will burn out eventually. No output available at HV transformer board. | iSCR driver board will still receive power from redundant HVT board. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Wear-out due to extensive use. Excessive humidity. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iSCR driver board. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 10 | [11 empty] | 5180
SV104 - 5181 | 24 V Feedback Signal Side 9 V Zener Diode. | D23 | To maintain a constant 9 V drop. To turn off the startup circuitry once full bridge auxiliary supply exceeds 9.1 V. | Diode fails-open. | 15 V regulator will keep on working from input side and will not turn off. Which will heat up the resistor on MOSFET Q6 drain and will burn out eventually. No output available at HV transformer board. | iSCR driver board will still receive power from redundant HVT board. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Mechanical stress or impact during assembly. Overcurrent. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iSCR driver board. | 2 | 4 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 20 | [11 empty] | 5181
SV104 - 5182 |  |  |  | Diode fails-short. | Startup circuitry will be turned off before full bridge secondary is activated completely. As a result startup circuitry will keep activating and then turn off due to aux voltage. This will eventually damage the startup circuitry of board. No output available at HV transformer board. | iSCR driver board will still receive power from redundant HVT board. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Mechanical stress or impact during assembly. Large reverse voltage. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iSCR driver board. | 2 | 4 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 20 | [11 empty] | 5182
SV104 - 6744 | 24 V Feedback Signal Side - R39 | R39 | Voltage divider resistor-Low side | Resistor fails-open | No immediate effect on board as Zener will keep voltage regulated at MOSFET gate. This will increase stress on Zener and affect Zener life. Board will stop working if Zener also gets damaged. Board will keep working normally. | iSCR driver board will still receive power from redundant HVT board. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Over voltage. Over Temperature. Over stress due to shock or vibration. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iSCR driver board. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 10 | [11 empty] | 6744
SV104 - 6745 |  |  |  | Resistor fails-short | 15 V regulator will keep on working from input side and will not turn off. Which will heat up the resistor on MOSFET Q6 drain and will burn out eventually. No output available at HV transformer board. | iSCR driver board will still receive power from redundant HVT board. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Wear-out due to extensive use. Excessive humidity. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iSCR driver board. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 10 | [11 empty] | 6745
SV104 - 6746 | 24 V Feedback Signal Side - D23 | D23 | To maintain a constant 9 V drop. To turn off the startup circuitry once full bridge auxiliary supply exceeds 9.1 V. | Diode fails-open | 15 V regulator will keep on working from input side and will not turn off. Which will heat up the resistor on MOSFET Q6 drain and will burn out eventually. No output available at HV transformer board. | iSCR driver board will still receive power from redundant HVT board. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Excessive forward current flow. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iSCR driver board. | 2 | 4 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 20 | [11 empty] | 6746
SV104 - 6747 |  |  |  | Diode fails-short | No immediate effect on board. | If no other failure is observed on the board, iSCR driver board will stay powered. Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | Large reverse voltage. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iSCR driver board. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [11 empty] | 6747
SV104 - 6748 | 24 V Feedback Signal Side - D24 | D24 | To prevent reverse power flow from startup circuitry | Diode fails-open | As soon as auxiliary will develop board will be disabled and power-up again and this cycle will keep repeating which will damage the startup circuitry permanently. No output available at HV transformer board. | iSCR driver board will still receive power from redundant HVT board. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Excessive forward current flow. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iSCR driver board. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 10 | [11 empty] | 6748
SV104 - 6749 |  |  |  | Diode fails-short | Startup circuitry will disable itself before powering up the board. It will happen repeatedly eventually damaging the startup circuitry. No output available at HV transformer board. | iSCR driver board will still receive power from redundant HVT board. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Large reverse voltage. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iSCR driver board. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 10 | [11 empty] | 6749
SV104 - 6750 | 24 V Feedback Signal Side - D26 | D26 | Overvoltage protection for MOSFET | Diode fails-open | No immediate effect on board. | If no other failure is observed on the board, iSCR driver board will stay powered. Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | Excessive forward current flow. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iSCR driver board. | 2 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 10 | [11 empty] | 6750
SV104 - 6751 |  |  |  | Diode fails-short | 15 V regulator will keep on working from input side and will not turn off. Which will heat up the resistor on MOSFET Q6 drain and will burn out eventually. No output available at HV transformer board. | iSCR driver board will still receive power from redundant HVT board. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Large reverse voltage. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iSCR driver board. | 2 | 4 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 20 | [11 empty] | 6751
SV104 - 5183 | 24 V Feedback Signal Side MOSFET. | Q7 | To turn OFF power flow controlling MOSFET when auxiliary voltage develops. | MOSFET fails-open. | 15 V regulator will keep on working from input side and will not turn off. Which will heat up the resistor on MOSFET Q6 drain and will burn out eventually. No output available at HV transformer board. | iSCR driver board will still receive power from redundant HVT board. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Overheating Mechanical stress resulting in cracked MOSFET body. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iSCR driver board. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 10 | [9 empty] | 0 |  | 5183
SV104 - 5184 |  |  |  | MOSFET fails-short. | Startup circuitry will remain off permanently as Q6 remains off permanently. 15 V regulator will keep on working from input side and will not turn off. Which will heat up the resistor on MOSFET Q6 drain and will burn out eventually. No output available at HV transformer board. | iSCR driver board will still receive power from redundant HVT board. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Transients Overheating as a result of loose connection with heat sink Overcurrent Counterfeit part Damage during mechanical assembly of board Metallic debris stuck in between terminals | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iSCR driver board. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 10 | [11 empty] | 5184
SV104 - 5185 | 24 V Feedback Signal Side MOSFET.- Zener at Gate | D25 | To protect MOSFET (Q6) gate from over-voltage. | Diode fails-open. | Over-voltage protection of MOSFET won't be available. No immediate effect on board in normal operations. | If no other failure is observed on the board, iSCR driver board will stay powered. Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | Mechanical stress or impact during assembly. Overcurrent. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 2 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 10 | [11 empty] | 5185
SV104 - 5186 |  |  |  | Diode fails-short. | Board will not power up as startup circuit will remain off. Q6 will remain permanently off. No output available at HV transformer board. | iSCR driver board will still receive power from redundant HVT board. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Large reverse voltage. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iSCR driver board. | 2 | 4 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 20 | [11 empty] | 5186
| PWM Controller | [26 empty] | 0
SV104 - 5187 | PWM Controller IC. | U1 | To provide alternate PWM pulses for full bridge gate driver. | IC output is permanently low. | No PWM will be available for half bridge driver ICs, No output available at HV transformer board. Redundant power to iSCR driver board will be cut-off. | iSCR driver board will still receive power from redundant HVT board. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Electrical Overstress. ESD. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iSCR driver board. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 10 | [9 empty] | 0 |  | 5187
SV104 - 5188 |  |  |  | One of output is permanently high. | Output of Full Bridge circuit will be 12 V at no load. HV transformer board will have no output as soon as load is applied. Redundant power to iSCR driver board will be cut-off. | iSCR driver board will still receive power from redundant HVT board. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Electrical Overstress. ESD. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iSCR driver board. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 10 | [9 empty] | 0 |  | 5188
SV104 - 5189 |  |  |  | PWM has a different duty cycle than desired. | Output of Full Bridge circuit will have different duty cycle. HV transformer board will have more or less than 24 V output. | If no other failure is observed on the board, iSCR driver board will stay powered. Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | Internal IC damage. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iSCR driver board. | 2 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 10 | [9 empty] | 0 |  | 5189
SV104 - 5190 | Line Under-Voltage Lockout Voltage Divider High Side Resistor. | R1 | To turn OFF gate driver PWM in case of under-voltage. | Resistor fails-open. | PWM controller will remain off permanently. No output available. | iSCR driver board will still receive power from redundant HVT board. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Over voltage. Over Temperature. Over stress due to shock or vibration. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iSCR driver board. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 10 | [9 empty] | 0 |  | 5190
SV104 - 5191 |  |  |  | Resistor fails-short. | UVLO pin will get damaged, No PWM will be available for half bridge driver ICs, No output available at HV transformer board. Redundant power to iSCR driver board will be cut-off. | iSCR driver board will still receive power from redundant HVT board. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Wear-out due to extensive use. Excessive humidity. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iSCR driver board. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 10 | [11 empty] | 5191
SV104 - 5192 | Line Under-Voltage Lockout Voltage Divider Low Side Resistor. | R13 | To turn OFF gate driver PWM in case of under-voltage. | Resistor fails-open. | UVLO pin will get damaged, No PWM will be available as IC will get damaged. No output available at HV transformer board. Redundant power to iSCR driver board will be cut-off. | iSCR driver board will still receive power from redundant HVT board. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Over voltage. Over Temperature. Over stress due to shock or vibration. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iSCR driver board. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 10 | [9 empty] | 0 |  | 5192
SV104 - 5193 |  |  |  | Resistor fails-short. | PWM controller will remain off permanently. No output available. | iSCR driver board will still receive power from redundant HVT board. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Wear-out due to extensive use. Excessive humidity. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iSCR driver board. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 10 | [11 empty] | 5193
SV104 - 5194 | RT2 Biasing Resistor. | R14 | To control oscillator dead time. | Resistor fails-open. | Dead time between alternating PWMs will be altered (maximum). Output of isolation transformer will be less. No output available at HV transformer board. Redundant power to iSCR driver board will be cut-off. | iSCR driver board will still receive power from redundant HVT board. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Over voltage. Over Temperature. Over stress due to shock or vibration. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iSCR driver board. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 10 | [9 empty] | 0 |  | 5194
SV104 - 5195 |  |  |  | Resistor fails-short. | Dead time between alternating PWMs will be altered (minimum). Switching losses will increase which will affect board life. Output of isolation transformer will be available. | If no other failure is observed on the board, iSCR driver board will stay powered. Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | Wear-out due to extensive use. Excessive humidity. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [11 empty] | 5195
SV104 - 5196 | RT1 Biasing Resistor. | R15 | To control oscillator maximum ON time. | Resistor fails-open. | Oscillator frequency will be altered to minimum. Switching frequency of converter will be changed as a result transformer can saturate. Output of isolation transformer will not be available. No output available at HV transformer board. Redundant power to iSCR driver board will be cut-off. | iSCR driver board will still receive power from redundant HVT board. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Over voltage. Over Temperature. Over stress due to shock or vibration. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iSCR driver board. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 10 | [9 empty] | 0 |  | 5196
SV104 - 5197 |  |  |  | Resistor fails-short. | Oscillator frequency will be altered (maximum). No immediate effect but core losses will increase and will effect board life. | iSCR driver board will still receive power from redundant HVT board. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Wear-out due to extensive use. Excessive humidity. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iSCR driver board. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 10 | [11 empty] | 5197
SV104 - 5198 | Restart Timer Resistor. | R16 | To set PWM restart signal biasing. | Resistor fails-open. | No immediate effect on board in normal operations. Hiccup mode current limiting will be activated. On detection of current limit the controller will turn off and will restart after a short time until current fault is removed. | If no other failure is observed on the board, iSCR driver board will stay powered. Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | Over voltage. Over Temperature. Over stress due to shock or vibration. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iSCR driver board. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [9 empty] | 0 |  | 5198
SV104 - 5199 |  |  |  | Resistor fails-short. | No immediate effect on board in normal operations. Cycle by cycle current limit will keep working. On current limit detection it skips some pulses instead of completely turning off controller like in hiccup mode. | If no other failure is observed on the board, iSCR driver board will stay powered. Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | Wear-out due to extensive use. Excessive humidity. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iSCR driver board. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [11 empty] | 5199
SV104 - 5200 | Soft-Start Capacitor. | C10 | To provide soft-start biasing value. | Capacitor fails-open. | Soft start will not be provided. No immediate effect on board. | If no other failure is observed on the board, iSCR driver board will stay powered. Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | Mechanical stress. Localized heating for long time will separate end connection of capacitor. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iSCR driver board. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [9 empty] | 0 |  | 5200
SV104 - 5201 |  |  |  | Capacitor fails-short. | PWM controller will turn off permanently. No output available for board. | iSCR driver board will still receive power from redundant HVT board. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Wear-out due to dielectric degradation. High-voltage transients. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iSCR driver board. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 10 | [11 empty] | 5201
SV104 - 5202 | Ramp Control Resistor. | R12 | To provide ramp control of PWM. | Resistor fails-open. | PWM ramp will be affected. Output of Full Bridge circuit will be different than desired. HV transformer board will have more or less than 24 V output. | If no other failure is observed on the board, iSCR driver board will stay powered. Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | Over voltage. Over Temperature. Over stress due to shock or vibration. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iSCR driver board. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [9 empty] | 0 |  | 5202
SV104 - 5203 |  |  |  | Resistor fails-short. | PWM ramp will be affected. Output of Full Bridge circuit will be different than desired. HV transformer board will have more or less than 24 V output. | If no other failure is observed on the board, iSCR driver board will stay powered. Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | Wear-out due to extensive use. Excessive humidity. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iSCR driver board. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [11 empty] | 5203
SV104 - 5204 | Current Sense Signal Filtration Capacitor. | C12 | To filter the CS signal. | Capacitor fails-open. | No immediate effect on board in normal operations. | If no other failure is observed on the board, iSCR driver board will stay powered. Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | Mechanical stress. Localized heating for long time will separate end connection of capacitor. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iSCR driver board. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [11 empty] | 5204
SV104 - 5205 |  |  |  | Capacitor fails-short. | Capacitor will fail-open due to over-current. PWM current limiting functionality will be compromised while the capacitor remains shorted. No immediate effect on board in normal operations. | If no other failure is observed on the board, iSCR driver board will stay powered. Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | Wear-out due to dielectric degradation. High-voltage transients. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iSCR driver board. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [11 empty] | 5205
SV104 - 5206 | Current Sense Capacitor. | C9 | To eliminate sub-harmonic oscillation | Capacitor fails-open. | No immediate effect on board in normal operations. | If no other failure is observed on the board, iSCR driver board will stay powered. Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | Mechanical stress. Localized heating for long time will separate end connection of capacitor. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iSCR driver board. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [9 empty] | 0 |  | 5206
SV104 - 5207 |  |  |  | Capacitor fails-short. | PWM current limiting functionality will be compromised if overcurrent situation occurs at primary side. No immediate effect on board in normal operations. | If no other failure is observed on the board, iSCR driver board will stay powered. Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | Wear-out due to dielectric degradation. High-voltage transients. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iSCR driver board. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [11 empty] | 5207
SV104-12380 | Decoupling Capacitor | C11 | To Filter Noise | Capacitor fails-open. | No immediate effect on board in normal operations. | If no other failure is observed on the board, iSCR driver board will stay powered. Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | Mechanical stress. Localized heating for long time will separate end connection of capacitor. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iSCR driver board. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. Vibration Testing. | None. | 5 | 5 | [11 empty] | 12380
SV104-12381 |  |  |  | Capacitor fails-short. | Internal Reference Voltage will be shorted to ground. PWM output will be disabled. No output available at HV transformer board. | iSCR driver board will still receive power from redundant HVT board. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Wear-out due to dielectric degradation. High-voltage transients. De-gradation of components. Water ingress during humidity condition as it is film capacitor. Overvoltage | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. RTV application on edges to stop water ingress. Redundant HV Transformer board to power-up iSCR driver board. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. Environmental Testing. | None. | 5 | 10 | [11 empty] | 12381
SV104-10923 | Input Filtration Capacitance | C1 | To suppress ripples on input voltage. | Capacitor fails-open. | No immediate effect on board due to presence of multiple capacitors at different stages.. | If no other failure is observed on the board, iSCR driver board will stay powered. Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | Mechanical stress. Localized heating for long time will separate end connection of capacitor. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iSCR driver board. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. Vibration Testing. | None. | 5 | 5 | [11 empty] | 10923
SV104-10924 |  |  |  | Capacitor fails-short. | 15V rail will get shorted to ground thus No output available at HV transformer board . | iSCR driver board will still receive power from redundant HVT board. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Wear-out due to dielectric degradation. High-voltage transients. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iSCR driver board. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 10 | [11 empty] | 10924
SV104-10925 | Current Sense Resistance | R28 | Filter to remove noise from current sense signal | Resistor fails-open. | Overcurrent Protection will be compromised during overcurrent condition at primary. No immediate Effect in normal condition. | If no other failure is observed on the board, iSCR driver board will stay powered. Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | Over voltage. Over Temperature. Over stress due to shock or vibration. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iSCR driver board. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [9 empty] | 0 |  | 10925
SV104-10926 |  |  |  | Resistor fails-short. | IC may trigger False overcurrent and disable output. No output available at HV transformer board | iSCR driver board will still receive power from redundant HVT board. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Wear-out due to extensive use. Excessive humidity. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iSCR driver board. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 10 | [11 empty] | 10926
SV104 - 5208 | Output Driver Resistor. | R4,R5 | To limit gate driver current. | Resistor fails-open. | Gate driver PWM path will be broken. No output available at HV transformer board. Redundant power to iSCR driver board will be cut-off. | iSCR driver board will still receive power from redundant HVT board. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Over voltage. Over Temperature. Over stress due to shock or vibration. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iSCR driver board. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 10 | [11 empty] | 5208
SV104 - 5209 |  |  |  | Resistor fails-short. | No immediate till the shorted duration. Resistor will fail-open due to over-current. Gate driver PWM path will be broken. No output available at HV transformer board. Redundant power to iSCR driver board will be cut-off. | iSCR driver board will still receive power from redundant HVT board. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Wear-out due to extensive use. Excessive humidity. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iSCR driver board. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 10 | [9 empty] | 0 |  | 5209
| Full Bridge Circuit | [26 empty] | 0
SV104 - 5210 | Half Bridge Gate Driver IC. | U2, U3 | To provide gate driver signal for half bridge MOSFETs. | Both outputs are permanently low. | One half bridge section will not have output. Output of Full Bridge circuit will be 12 V at no load. HV transformer board will have no output as soon as load is applied. Redundant power to iSCR driver board will be cut-off. | iSCR driver board will still receive power from redundant HVT board. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Electrical Overstress (Overvoltage). ESD. Counterfeit part. Stress or impact during assembly. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iSCR driver board. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 10 | [11 empty] | 5210
SV104 - 5211 |  |  |  | High side output is permanently low. | Full bridge functionality will be disturbed. No output will be available at HV transformer board as soon as load is applied. | iSCR driver board will still receive power from redundant HVT board. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Electrical Overstress (Overvoltage). ESD. Counterfeit part. Stress or impact during assembly. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iSCR driver board. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 10 | [11 empty] | 5211
SV104 - 5212 |  |  |  | High side output is permanently high. | One MOSFET will be permanently turned ON. During times, when low side MOSFET of same half bridge will turn ON, HV DC line get shorted will ground. Due to high current flow, power MOSFETs may get damaged. Input side fuse will burn out and prevent cascading failures. | iSCR driver board will still receive power from redundant HVT board. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Electrical Overstress (Overvoltage). ESD. Counterfeit part. Stress or impact during assembly. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iSCR driver board. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 10 | [11 empty] | 5212
SV104 - 8896 | Half Bridge Gate Driver IC. | U2, U3 | To provide gate driver signal for half bridge MOSFETs. | Low side output is permanently low. | Full bridge functionality will be disturbed. No output will be available at HV transformer board as soon as load is applied. | iSCR driver board will still receive power from redundant HVT board. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Electrical Overstress (Overvoltage). ESD. Counterfeit part. Stress or impact during assembly. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iSCR driver board. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 10 | [11 empty] | 8896
SV104 - 8897 |  |  |  | Low side output is permanently high. | During times, when high side MOSFET of same half bridge will turn ON, HV DC line get shorted with ground. Due to high current flow, power MOSFETs may get damaged. Input side fuse will burn out and prevent cascading failures. | iSCR driver board will still receive power from redundant HVT board. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Electrical Overstress (Overvoltage). ESD. Counterfeit part. Stress or impact during assembly. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iSCR driver board. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 10 | [11 empty] | 8897
SV104 - 8898 |  |  |  | Both outputs are permanently high. | Both MOSFETs will be permanently turned ON. HV DC line will get shorted with ground. Due to high current flow, power MOSFETs may get damaged. Input side fuse will burn out and prevent cascading failures. | iSCR driver board will still receive power from redundant HVT board. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Electrical Overstress (Overvoltage). ESD. Counterfeit part. Stress or impact during assembly. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iSCR driver board. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 10 | [11 empty] | 8898
SV104 - 5213 | Half Bridge Gate Driver IC - Filter Capacitor. | C4,C5 | To provide high side gate driver floating supply. | Capacitor fails-open. | Output of gate driver IC will be affected. No output available at HV transformer board. Redundant power to iSCR driver board will be cut-off. . | iSCR driver board will still receive power from redundant HVT board. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Mechanical stress. Localized heating for long time will separate end connection of capacitor. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iSCR driver board. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 10 | [11 empty] | 5213
SV104 - 5214 |  |  |  | Capacitor fails-short. | Output of gate driver IC will be affected. No output available at HV transformer board. Redundant power to iSCR driver board will be cut-off. . | iSCR driver board will still receive power from redundant HVT board. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Wear-out due to dielectric degradation. High-voltage transients. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iSCR driver board. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 10 | [11 empty] | 5214
SV104 - 5215 | Gate Driver Output Circuit - Resistor. | R7,R24,R6,R23 | To provide path between gate driver IC and gate. | Resistor fails-open. | Output path of gate driver IC will be broken for one MOSFET. Distorted square wave will be available at full bridge circuit output. HV transformer board will have lesser output than desired. | iSCR driver board will still receive power from redundant HVT board. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Over voltage. Over Temperature. Over stress due to shock or vibration. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iSCR driver board. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 10 | [11 empty] | 5215
SV104 - 5216 |  |  |  | Resistor fails-short. | Over-current will cause the resistor to eventually fail-open. Output path of gate driver IC will be broken for one MOSFET. Distorted square wave will be available at full bridge circuit output. HV transformer board will have lesser output than desired. | iSCR driver board will still receive power from redundant HVT board. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Wear-out due to extensive use. Excessive humidity. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iSCR driver board. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 10 | [11 empty] | 5216
SV104 - 5217 | Gate Driver Output Circuit - General Purpose Diode. | D1,D2,D3,D4 | To turn off the MOSFET quickly through low resistance path at gate. | Diode fails-open. | MOSFET will turn off through larger resistor which will result in increased switching losses. No immediate effect in case of normal operations. | If no other failure is observed on the board, iSCR driver board will stay powered. Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | Mechanical stress or impact during assembly. Overcurrent. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iSCR driver board. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [11 empty] | 5217
SV104 - 5218 |  |  |  | Diode fail-short. | Over-current will cause the diode to eventually fail-open. MOSFET will turn off through larger resistor which will result in increased switching losses. No immediate effect in case of normal operations. | If no other failure is observed on the board, iSCR driver board will stay powered. Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | Large reverse voltage. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [11 empty] | 5218
SV104-10927 | Gate Driver Output Circuit -Discharge Resistor. | R2,R3,R20,R21 | To provide low resistance path between gate driver IC and gate to discharge miller capacitance. | Resistor fails-open. | Gate Capacitance will discharge slowly through high resistance path thus on/off time will be disturbed Switching losses will increase. No immediate effect ion board. | If no other failure is observed on the board, iSCR driver board will stay powered. Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | Over voltage. Over Temperature. Over stress due to shock or vibration. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iSCR driver board. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [11 empty] | 10927
SV104-10928 |  |  |  | Resistor fails-short. | Switching losses will increase. No immediate effect on board. | If no other failure is observed on the board, iSCR driver board will stay powered. Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | Wear-out due to extensive use. Excessive humidity. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iSCR driver board. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [11 empty] | 10928
SV104-10929 | MOSFET resistance for Miller Capacitance | R10,R27,R11,R26 | To discharge miller capacitances between all terminals of MOSFET | Resistor fails-open | Abnormal Behavior of MOSFET Might turn ON/OFF abnormally and can damage board. No output available at HV transformer board | iSCR driver board will still receive power from redundant HVT board. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Over voltage. Over Temperature. Over stress due to shock or vibration. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iSCR driver board. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. Vibration testing. | None. | 5 | 10 | [11 empty] | 10929
SV104-10930 |  |  |  | Resistor fails-short | Gate and Source of MOSFET will have no voltage difference so MOSFET cannot operate No output available at HV transformer board | iSCR driver board will still receive power from redundant HVT board. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Wear-out due to extensive use. Excessive humidity. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iSCR driver board. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. Vibration testing. | None. | 5 | 10 | [11 empty] | 10930
SV104-10931 | Half Bridge Gate Driver IC - High Side Supply Capacitor. | C7,C15,C16,C8 | To provide high side supply and to ensure bootstrapping in order to operate MOSFET. | One Capacitor fails-open. | No immediate effect as the parallel capacitor will be available and will make sure that MOSFET works properly | If no other failure is observed on the board, iSCR driver board will stay powered. Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | Mechanical stress. Localized heating for long time will separate end connection of capacitor. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iSCR driver board. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [11 empty] | 10931
SV104-10932 |  |  |  | Both Capacitors fails-open. | MOSFET Cannot operate properly No output available at HV transformer board | iSCR driver board will still receive power from redundant HVT board. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Mechanical stress. Localized heating for long time will separate end connection of capacitor. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iSCR driver board. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 10 | [11 empty] | 10932
SV104-10933 |  |  |  | Capacitor fails-short. | MOSFET Cannot operate properly IC may get damaged No output available at HV transformer board | iSCR driver board will still receive power from redundant HVT board. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Wear-out due to dielectric degradation. High-voltage transients. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iSCR driver board. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 10 | [11 empty] | 10933
SV104 - 5219 | Full Bridge Circuit - MOSFET | Q1,Q2,Q3,Q4 | To convert HV DC to HV AC signal. | MOSFET fails-open. | Distorted square wave will be available at full bridge circuit output. HV transformer board will have lesser output than desired. | iSCR driver board will still receive power from redundant HVT board. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Overheating Mechanical stress resulting in cracked MOSFET body. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iSCR driver board. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 10 | [11 empty] | 5219
SV104 - 5220 |  |  |  | MOSFET fails-short. | No voltage will be available at transformer output, for the shorted duration. No output available at HV transformer board. Redundant power to iSCR driver board will be cut-off. . | iSCR driver board will still receive power from redundant HVT board. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Transients Overheating as a result of loose connection with heat sink Overcurrent Counterfeit part Damage during mechanical assembly of board Metallic debris stuck in between terminals | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iSCR driver board. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 10 | [11 empty] | 5220
SV104-10934 | Full bridge circuit -Current sense resistors. | R29,R8 | To provide current sense signal to controller | One Resistor fails-open. | Over Current limit value will decrease down to half. No immediate affect in normal condition but in case of overloaded condition current limit will be activated early. | If no other failure is observed on the board, iSCR driver board will stay powered. Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | Over voltage. Over Temperature. Over stress due to shock or vibration. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iSCR driver board. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [11 empty] | 10934
SV104-10935 |  |  |  | Both Resistors fails-open. | Full bridge circuit ground connection will be disconnected No output available at HV transformer board | iSCR driver board will still receive power from redundant HVT board. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Over voltage. Over Temperature. Over stress due to shock or vibration. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iSCR driver board. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 10 | [11 empty] | 10935
SV104-10936 |  |  |  | Resistor fails-short. | No immediate effect in case of normal operations. Overcurrent protection will not be available. | If no other failure is observed on the board, iSCR driver board will stay powered. Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | Wear-out due to extensive use. Excessive humidity. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iSCR driver board. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [11 empty] | 10936
SV104 - 5221 | HV Isolation Transformer | P113720 | To step down 400 V AC to 24 V AC. | Primary winding fails-open. | No voltage will be available at transformer output. No output available at HV transformer board. Redundant power to iSCR driver board will be cut-off. . | iSCR driver board will still receive power from redundant HVT board. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | High operating temperature. Overloading | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iSCR driver board. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 10 | [11 empty] | 5221
SV104 - 5222 |  |  |  | Secondary winding fails-open. | No output available. Redundant power to one of the iSCR driver board will be cut-off. | iSCR driver board will still receive power from redundant HVT board. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | High operating temperature. Overloading | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iSCR driver board. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 10 | [11 empty] | 5222
SV104 - 5223 |  |  |  | Core degradation. | Output voltage will be less than desired value. | iSCR driver board will still receive power from redundant HVT board. Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | Mechanical Stress | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iSCR driver board. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [9 empty] | 0 |  | 5223
SV104 - 5224 |  |  |  | Winding insulation melting. | Turn ratio of transformer will be affected. Output voltage will be less than desired value. | iSCR driver board will still receive power from redundant HVT board. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Over voltage. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iSCR driver board. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 10 | [11 empty] | 5224
SV104 - 6752 |  |  |  | Isolation Failure. | If failure is such that board cannot provide any level of isolation then it will damage iSCR driver board. iSCR driver board will not be powered up. | In case of complete isolation failure, SCRs will not be available during mode transition and fault handling in one direction. Device can operate normally at lower line currents. In case of faults, VSLs and device internals might get damaged. | Affected device and associated group will not be able to enter injection mode. System will keep working normally with reduced injection capability. | 5 | Temperature cycling. Manufacturing Deficiency. Vibration. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 5 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 25 | [9 empty] | 0 |  | 6752
SV104 - 6753 |  |  |  | Auxiliary winding failure(Open) | No auxiliary voltage will be available. Startup circuit will not shutdown eventually burning out. No output will be available for HV-ISO board | iSCR driver board will still receive power from redundant HVT board. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Over voltage. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 10 | [11 empty] | 6753
SV104 - 6754 |  |  |  | Post insulator fails | Under normal working conditions, failure will not impact the working of the board. If failure is such that board cannot provide any level of isolation then it will damage iSCR driver board in humid conditions. iSCR driver board will not be powered up. | In case of complete isolation failure, SCRs will not be available during mode transition and fault handling in one direction. Device can operate normally at lower line currents. In case of faults, VSLs and device internals might get damaged. | Affected device and associated group will not be able to enter injection mode. System will keep working normally with reduced injection capability. | 5 | Corrosion. Manufacturing Deficiency. Vibration. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 5 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 25 | [9 empty] | 0 |  | 6754
SV104 - 6755 |  |  |  | Potting crack or physical damage | Partial discharge will start resulting in degradation of isolation barrier with the time. It will not be critical as isolation of even 400 Vrms will be enough. | If no other failure is observed on the board, iSCR driver board will stay powered. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Temperature variations Manufacturing Deficiency. Vibration. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 10 | [9 empty] | 0 |  | 6755
SV104 - 5225 | HV Isolation Transformer - output Side Full Rectifier - Diode | D5,D6,D8 | To convert 24 V AC to 24 V DC. | Diode fails-open. | Output cut to half if half side is working. Redundant power to iSCR driver board will be cut-off. . | iSCR driver board will still receive power from redundant HVT board. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Mechanical stress or impact during assembly. Overcurrent. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iSCR driver board. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 10 | [9 empty] | 0 |  | 5225
SV104 - 5226 |  |  |  | Diode fails-short. | Secondary winding will get shorted if any diode fails-short. As a result of shortage, excessive amount of current will flow damaging two diodes permanently. Diodes will eventually get open and no output will be available Redundant power to iSCR driver board will be cut-off. . | iSCR driver board will still receive power from redundant HVT board. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Large reverse voltage. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iSCR driver board. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 10 | [9 empty] | 0 |  | 5226
SV104 - 5229 | Output Side Capacitor. | C13,C14 | To suppress output side ripples and to provide filtration. | Capacitor fails-open. | Output voltage may have ripples. No immediate effect on HV transformer board output. | If no other failure is observed on the board, iSCR driver board will stay powered. Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | Mechanical stress. Localized heating for long time will separate end connection of capacitor. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iSCR driver board. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [9 empty] | 0 |  | 5229
SV104 - 5230 |  |  |  | Capacitor fails-short. | No voltage available at the output for the shorted duration. Redundant power to iSCR driver board will be cut-off. . | iSCR driver board will still receive power from redundant HVT board. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Wear-out due to dielectric degradation. High-voltage transients. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iSCR driver board. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 10 | [9 empty] | 0 |  | 5230
SV104 - 5227 | HV Isolation Transformer - Feedback Side Full Rectifier - Diode | D15,D16,D19,D20 | To convert 24 V AC to 24 V DC for feedback. | Diode fails-open. | Output cut to half if half side is working. Redundant power supply to iSCR board will be cut off. | iSCR driver board will still receive power from redundant HVT board. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Mechanical stress or impact during assembly. Overcurrent. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iSCR driver board. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 10 | [9 empty] | 0 |  | 5227
SV104 - 5228 |  |  |  | Diode fails-short. | Secondary winding will get shorted if any diode fails-short. As a result of shortage, excessive amount of current will flow damaging two diodes permanently. Diodes will eventually get open and no output will be available Redundant power to iSCR driver board will be cut-off. . | iSCR driver board will still receive power from redundant HVT board. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Large reverse voltage. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iSCR driver board. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 10 | [9 empty] | 0 |  | 5228
SV104 - 5229 | Output Side Capacitor. | C17,C18 | To suppress output side ripples and to provide filtration. | Capacitor fails-open. | Output voltage may have ripples. No immediate effect on HV transformer board output. | If no other failure is observed on the board, iSCR driver board will stay powered. Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | Mechanical stress. Localized heating for long time will separate end connection of capacitor. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iSCR driver board. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [9 empty] | 0 |  | 5229
SV104 - 5230 |  |  |  | Capacitor fails-short. | No voltage available at the output for the shorted duration. Redundant power to iSCR driver board will be cut-off. . | iSCR driver board will still receive power from redundant HVT board. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Wear-out due to dielectric degradation. High-voltage transients. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iSCR driver board. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 10 | [9 empty] | 0 |  | 5230
SV104-10937 | Current Limiting resistance for LED (D9) | R44 | To limit current through the LED (D9) | Resistor fails-open | LED indication functionality will be compromised No immediate effect on HV transformer board output. | If no other failure is observed on the board, iSCR driver board will stay powered. Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | Over voltage. Over Temperature. Over stress due to shock or vibration. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iSCR driver board. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. Vibration testing. | None. | 5 | 5 | [9 empty] | 0 |  | 10937
SV104-10938 |  |  |  | Resistor fails-short | LED indication functionality will be compromised No immediate effect on HV transformer board output. | If no other failure is observed on the board, iSCR driver board will stay powered. Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | Wear-out due to extensive use. Excessive humidity. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iSCR driver board. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. Vibration testing. | None. | 5 | 5 | [9 empty] | 0 |  | 10938
SV104-10939 | LED for status indication of voltage produced | D9 | Visual indication for board output status | Diode fails-open | LED indication functionality will be compromised No immediate effect on HV transformer board output. | If no other failure is observed on the board, iSCR driver board will stay powered. Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | Over voltage. Over Temperature. Over stress due to shock or vibration. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iSCR driver board. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. Vibration testing. | None. | 5 | 5 | [9 empty] | 0 |  | 10939
SV104-10940 |  |  |  | Diode fails-short. | LED indication functionality will be compromised No immediate effect on HV transformer board output. | If no other failure is observed on the board, iSCR driver board will stay powered. Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | Wear-out due to extensive use. Excessive humidity. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iSCR driver board. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. Vibration testing. | None. | 5 | 5 | [9 empty] | 0 |  | 10940
SV104-10941 | Load at output | R42,R43 | To keep open load voltage within a range | Resistor fails-open | No immediate effect on board. | If no other failure is observed on the board, iSCR driver board will stay powered. Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | Over voltage. Over Temperature. Over stress due to shock or vibration. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iSCR driver board. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. Vibration testing. | None. | 5 | 5 | [9 empty] | 0 |  | 10941
SV104-10942 |  |  |  | Resistor fails-short | 24V supply will be shorted out to ground. Resistance will eventually fail open due to over current. No output available at HV transformer board | iSCR driver board will still receive power from redundant HVT board. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Wear-out due to extensive use. Excessive humidity. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iSCR driver board. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. Vibration testing. | None. | 5 | 10 | [9 empty] | 0 |  | 10942
SV104-11403 | Secondary Winding Connector | J2 | Secondary of transformer | Connector Disconnected by external Force. | Secondary winding will be opened. No output available at HV transformer board. | iSCR driver board will still receive power from redundant HVT board. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Open Connections due to vibrations, mis-handling or mechanical stress. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iSCR driver board. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. Vibration Testing. | None. | 5 | 10 | [9 empty] | 0 |  | 11403
SV104-11404 |  |  |  | Connector Burned out | Due to sparking connector will heat up and eventually burnout No output available at HV transformer board. | iSCR driver board will still receive power from redundant HVT board. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Connection Loose or Sparking at terminals Open Connections due to vibrations, mis-handling or mechanical stress. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iSCR driver board. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. Vibration Testing. | None. | 5 | 10 | [9 empty] | 0 |  | 11404
SV104-11405 | Low voltage DC output Connector | J4 | Output of HVT board | Connector Disconnected by external Force. | Output path will be broken. No output available at HV transformer board. | iSCR driver board will still receive power from redundant HVT board. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Open Connections due to vibrations, mis-handling or mechanical stress. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iSCR driver board. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. Vibration Testing. | None. | 5 | 10 | [9 empty] | 0 |  | 11405
SV104-11406 |  |  |  | Connector Burned out | Due to sparking connector will heat up and eventually burnout Output path will be broken. No output available at HV transformer board. | iSCR driver board will still receive power from redundant HVT board. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Connection Loose or Sparking at terminals Open Connections due to vibrations, mis-handling or mechanical stress. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iSCR driver board. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. Vibration Testing. | None. | 5 | 10 | [9 empty] | 0 |  | 11406
SV104-11407 | Auxiliary winding Connector | J6 | Auxiliary winding of transformer for 24AUX | Connector Disconnected by external Force. | 24AUX path will be broken. Startup circuitry will turn on permanently resulting in overheating and permanently damage to startup resistor. No output available once HV-ISO reboot. | iSCR driver board will still receive power from redundant HVT board. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Open Connections due to vibrations, mis-handling or mechanical stress. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iSCR driver board. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. Vibration Testing. | None. | 5 | 10 | [9 empty] | 0 |  | 11407
SV104-11408 |  |  |  | Connector Burned out | Due to sparking connector will heat up and eventually burnout 24AUX path will be broken. Startup circuitry will turn on permanently resulting in overheating and permanently damage to startup resistor. No output available once HV-ISO reboot. | iSCR driver board will still receive power from redundant HVT board. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Connection Loose or Sparking at terminals Open Connections due to vibrations, mis-handling or mechanical stress. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iSCR driver board. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. Vibration Testing. | None. | 5 | 10 | [9 empty] | 0 |  | 11408
SV104-11409 | Primary winding of transformer | J1,J5 | primary winding of transformer | Connector Disconnected by external Force. | No voltage will be available at transformer output. No output available at HV transformer board. | iSCR driver board will still receive power from redundant HVT board. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Open Connections due to vibrations, mis-handling or mechanical stress. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iSCR driver board. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. Vibration Testing. | None. | 5 | 10 | [9 empty] | 0 |  | 11409
SV104-11410 |  |  |  | Connector Burned out | Due to sparking connector will heat up and eventually burnout No voltage will be available at transformer output. No output available at HV transformer board. | iSCR driver board will still receive power from redundant HVT board. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Connection Loose or Sparking at terminals Open Connections due to vibrations, mis-handling or mechanical stress. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iSCR driver board. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. Vibration Testing. | None. | 5 | 10 | [11 empty] | 11410
SV104 - 5231 | Heat Sink | HS1,HS2,HS3,HS4,HS5,HS6,HS7,HS8. | To provide cooling functionality for power components. | Loose connection between heat sink and power component. | Affected component will face high temperature rise during nominal current operations. Power component may get damaged causing HV transformer board output voltage to drop. Redundant power to iSCR driver board will be cut-off. . | iSCR driver board will still receive power from redundant HVT board. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | External overstress. Mis-handling. Excessive temperature causing joint melts. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iSCR driver board. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 10 | [11 empty] | 5231
| HV Transformer Board for one iVSL Driver Board | [26 empty] | 0
| 15 V On-Board Supply | [26 empty] | 0
SV104 - 5232 | Input Side TRIACs. | D13,D12 | Reverse polarity protection. | TRIAC fails-open. | No immediate effect. Parallel TRIAC available for alternate path. | If no other failure is observed on the board, iVSL driver board will stay powered. Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | On-board fault causing higher current flow. Excessive forward current. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant 24 V supply to iVSL Driver boards will be provided via UPSB. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [11 empty] | 5232
SV104 - 5233 |  |  |  | TRIAC fails-short. | Reverse polarity protection will be compromised during shortage. Board will keep working normally if input is provided with correct polarity. | If no other failure is observed on the board, iVSL driver board will stay powered. Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | Large reverse voltage. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant 24 V supply to iVSL Driver boards will be provided via UPSB. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [9 empty] | 0 |  | 5233
SV104 - 6756 |  |  |  | Both TRIACs fail-short. | Reverse polarity protection will be compromised. Board will keep working normally if input is provided with correct polarity. | If no other failure is observed on the board, iVSL driver board will stay powered. Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | Large reverse voltage. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant 24 V supply to iVSL Driver boards will be provided via UPSB. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [11 empty] | 6756
SV104 - 6757 |  |  |  | Both TRIACs fail-open | Input path will be broken. No output available at HV transformer board. | Redundant power to one of the iVSL driver board will be cut-off. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | On-board fault causing higher current flow. Excessive forward current. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant 24 V supply to iVSL Driver boards will be provided via UPSB. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 10 | [11 empty] | 6757
SV104 - 5234 | Input Side Fuse. | F2 | To cut-off supply in case of over-current. | Fuse fails-open. | Input power path will be broken. No output available at HV transformer board. | Redundant power to one of the iVSL driver board will be cut-off. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | On-board fault causing higher current flow. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant 24 V supply to iVSL Driver boards will be provided via UPSB. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 10 | [11 empty] | 5234
SV104 - 5235 | Input Side Filter Capacitors. | C2,C23 | To suppress ripples on input voltage. | Capacitor fails-open. | Input supply ripples may cause distorted output supply. No immediate effect on board.. | If no other failure is observed on the board, iVSL driver board will stay powered. Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | Mechanical stress. Localized heating for long time will separate end connection of capacitor. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant 24 V supply to iVSL Driver boards will be provided via UPSB. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [11 empty] | 5235
SV104 - 5236 |  |  |  | Capacitor fails-short. | PHT-DC capacitors will be shorted as a result will dump full energy in HV-ISO board. HV-ISO board input traces will be damaged. No output available at HV transformer board. | Redundant power to one of the iVSL driver board will be cut-off. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Wear-out due to dielectric degradation. High-voltage transients. De-gradation of components. Water ingress during humidity condition as it is film capacitor. Overvoltage | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. RTV application to stop water ingress Redundant 24 V supply to iVSL Driver boards will be provided via UPSB. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. Environmental Testing. | None. | 5 | 10 | [11 empty] | 5236
SV104 - 5237 | Low Voltage Detection Zener Diode. (D7, D11, D10) | D7,D10,D11 | To set under-voltage lockout threshold. | Diode fails-open. | No voltage will be available at power controlling MOSFET gate. On-board 15 V supply will not be available. No output available at HV transformer board. Redundant power to one of the iVSL driver board via HVT will be cut-off. | Redundant power to one of the iVSL driver board will be cut-off. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Mechanical stress or impact during assembly. Overcurrent. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant 24 V supply to iVSL Driver boards will be provided via UPSB. | 2 | 4 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 20 | [11 empty] | 5237
SV104 - 5238 |  |  |  | Diode fails-short.. | The threshold for UVLO detection will decrease. Board will turn on before the set threshold of 320 V. Slight effect will be on PHT-DC bus during low line current condition as it will ramp up slowly. Board will keep working. | If no other failure is observed on the board, iVSL driver board will stay powered. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Large reverse voltage. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant 24 V supply to iVSL Driver boards will be provided via UPSB. | 2 | 4 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 20 | [11 empty] | 5238
SV104-10943 | Low Voltage Detection Voltage Divider | R41,R36 | To set UVLO threshold | Resistor fails-open. | No voltage will be available at power controlling MOSFET gate. On-board 15 V supply will not be available. No output available at HV transformer board. | Redundant power to one of the iVSL driver board will be cut-off. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Over voltage. Over Temperature. Over stress due to shock or vibration. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant 24 V supply to iVSL Driver boards will be provided via UPSB. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. Vibration testing. | None. | 5 | 10 | [11 empty] | 10943
SV104-10944 |  |  |  | Resistor fails-short. | UVLO limit will decrease. Board will powerup at lower voltage. Board will keep working. | If no other failure is observed on the board, iVSL driver board will stay powered. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Wear-out due to extensive use. Excessive humidity. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant 24 V supply to iVSL Driver boards will be provided via UPSB. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. Vibration testing. | None. | 5 | 10 | [11 empty] | 10944
SV104 - 5239 | Input Side Voltage Divider Resistor. | R30,R31,R32,R33,R34,R35 | To step down voltage. | Resistor fails-open. | No voltage will be available at power controlling MOSFET gate. On-board 15 V supply will not be available. No output available at HV transformer board. . | Redundant power to one of the iVSL driver board will be cut-off. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Over voltage. Over Temperature. Over stress due to shock or vibration. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant 24 V supply to iVSL Driver boards will be provided via UPSB. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 10 | [9 empty] | 0 |  | 5239
SV104 - 5240 |  |  |  | Any one resistor fails-short. | No immediate effect on board. Board will keep working normally. | If no other failure is observed on the board, iVSL driver board will stay powered. Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | Wear-out due to extensive use. Excessive humidity. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant 24 V supply to iVSL Driver boards will be provided via UPSB. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [11 empty] | 5240
SV104-12382 |  |  |  | More than one resistors fails-short. | Soft starting current is increased significantly consequently MOSFET power dissipation will increase that could bring failure. No output available at HV transformer board. | Redundant power to one of the iVSL driver board will be cut-off. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Wear-out due to extensive use. Excessive humidity. Counterfeit part. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements.. Conformal coating. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. Vibration testing. | None. | 5 | 10 | [11 empty] | 12382
SV104 - 5241 | Input Power Control MOSFET. | Q6 | To turn ON/OFF power flow. | MOSFET fails-open. | Input power path will be broken. No output available at HV transformer board. | Redundant power to one of the iVSL driver board will be cut-off. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Overheating Mechanical stress resulting in cracked MOSFET body. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant 24 V supply to iVSL Driver boards will be provided via UPSB. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 10 | [9 empty] | 0 |  | 5241
SV104 - 5242 |  |  |  | MOSFET fails-short. | Startup circuitry will turn on permanently resulting in overheating and permanently damage to startup resistor. No output available once HV-ISO reboot | Redundant power to one of the iVSL driver board will be cut-off. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Transients Overheating as a result of loose connection with heat sink Overcurrent Counterfeit part Damage during mechanical assembly of board Metallic debris stuck in between terminals | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant 24 V supply to iVSL Driver boards will be provided via UPSB. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 10 | [11 empty] | 5242
SV104 - 5243 | Over-voltage Protection Zener Diode at MOSFET Gate Side. | D31 | For gate protection of MOSFET. | Diode fails-open. | Over-voltage protection of MOSFET won't be available. No immediate effect on board in normal operations. | If no other failure is observed on the board, iVSL driver board will stay powered. Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | Mechanical stress or impact during assembly. Overcurrent. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant 24 V supply to iVSL Driver boards will be provided via UPSB. | 2 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 10 | [11 empty] | 5243
SV104 - 5244 |  |  |  | Diode fails-short. | MOSFET will be turned off completely. Startup circuit will not work. No output available at HV transformer board. | Redundant power to one of the iVSL driver board will be cut-off. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Large reverse voltage. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant 24 V supply to iVSL Driver boards will be provided via UPSB. | 2 | 4 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 20 | [11 empty] | 5244
SV104-12383 | Filtration Capacitor | C21 | To suppress noise and remove ripples | Capacitor fails-open. | No immediate effect on board. Board will keep working normally. | If no other failure is observed on the board, iVSL driver board will stay powered. Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | Mechanical stress. Localized heating for long time will separate end connection of capacitor. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant 24 V supply to iVSL Driver boards will be provided via UPSB. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. Vibration Testing. | None. | 5 | 5 | [9 empty] | 0 |  | 12383
SV104-12384 |  |  |  | Capacitor fails-short. | HVDC and 24VAUX will be shorted top ground. Startup circuit will not work. Input Fuse Will be Blown No output available at HV transformer board. | Redundant power to one of the iVSL driver board will be cut-off. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Wear-out due to dielectric degradation. High-voltage transients. De-gradation of components. Water ingress during humidity condition as it is film capacitor. Overvoltage | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant 24 V supply to iVSL Driver boards will be provided via UPSB. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. Environmental Testing. | None. | 5 | 10 | [11 empty] | 12384
SV104-10945 | MOSFET resistance for Miller Capacitance | R37 | To discharge miller capacitance of MOSFET | Resistor fails-open | Abnormal Behavior of MOSFET Might turn ON/OFF abnormally. Once Board Reboots no output will be available No output available at HV transformer board | Redundant power to one of the iVSL driver board will be cut-off. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Over voltage. Over Temperature. Over stress due to shock or vibration. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant 24 V supply to iVSL Driver boards will be provided via UPSB. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. Vibration testing. | None. | 5 | 10 | [9 empty] | 0 |  | 10945
SV104-10946 |  |  |  | Resistor fails-short | Gate and Source of Q6 will have no voltage difference so MOSFET cannot operate No output available at HV transformer board | Redundant power to one of the iVSL driver board will be cut-off. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Wear-out due to extensive use. Excessive humidity. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant 24 V supply to iVSL Driver boards will be provided via UPSB. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. Vibration testing. | None. | 5 | 10 | [11 empty] | 10946
SV104 - 6758 | D21-Free wheeling diode | D21 | To protect BJT during reverse voltage condition | Diode fails-open. | No protection for BJT will be available. Reverse voltage development across BJT will damage it. No output available. | Redundant power to one of the iVSL driver board will be cut-off. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Mechanical stress or impact during assembly. Overcurrent. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant 24 V supply to iVSL Driver boards will be provided via UPSB. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 10 | [11 empty] | 6758
SV104 - 6759 |  |  |  | Diode fails-short. | Input will appear as it is on output which will damage PWM controller and gate driver ICs permanently. No output available. | Redundant power to one of the iVSL driver board will be cut-off. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Large reverse voltage. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant 24 V supply to iVSL Driver boards will be provided via UPSB. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 10 | [11 empty] | 6759
SV104 - 6760 | D22-To prevent reverse power flow | D22 | To prevent reverse power flow from auxiliary to startup circuitry | Diode fails-open. | Input power path will be broken. No output available at HV transformer board. | Redundant power to one of the iVSL driver board will be cut-off. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Mechanical stress or impact during assembly. Overcurrent. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant 24 V supply to iVSL Driver boards will be provided via UPSB. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 10 | [11 empty] | 6760
SV104 - 6761 |  |  |  | Diode fails-short. | If the board is OFF than it can not turn ON. If board is ON than reverse power will start to flow. D31 will be forward biased and as gate of Q6 is grounded than 24VAUX will also be grounded. No output available at HV transformer board. | Redundant power to one of the iVSL driver board will be cut-off. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Large reverse voltage. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant 24 V supply to iVSL Driver boards will be provided via UPSB. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 10 | [11 empty] | 6761
SV104 - 6762 | D27-Zener diode | D27 | To set reference voltage for BJT to regulate | Diode fails-open. | Voltage at input will appear as it is on base damaging it permanently. No output available at HV transformer board. | Redundant power to one of the iVSL driver board will be cut-off. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Mechanical stress or impact during assembly. Overcurrent. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant 24 V supply to iVSL Driver boards will be provided via UPSB. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 10 | [11 empty] | 6762
SV104 - 6763 |  |  |  | Diode fails-short. | BJT will not turn on. No output available at HV transformer board. | Redundant power to one of the iVSL driver board will be cut-off. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Large reverse voltage. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant 24 V supply to iVSL Driver boards will be provided via UPSB. | 2 | 4 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 20 | [11 empty] | 6763
SV104 - 5245 | Input Power Control BJT. | Q8 | To provide regulated voltage for startup. | BJT fails-open. | Input power path will be broken. No output available at HV transformer board. | Redundant power to one of the iVSL driver board will be cut-off. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Melted connections due to overheating. Manufacturing defect. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant 24 V supply to iVSL Driver boards will be provided via UPSB. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 10 | [11 empty] | 5245
SV104 - 5246 |  |  |  | BJT fails-short. | Higher voltage at startup will damage the PWM controller and gate drivers of board. Input power path will be broken. No output available at HV transformer board. | Redundant power to one of the iVSL driver board will be cut-off. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Over voltage. Leaky junctions. Wear-out due to high power dissipation. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant 24 V supply to iVSL Driver boards will be provided via UPSB. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 10 | [11 empty] | 5246
SV104 - 5247 | Biasing Resistor for BJT. | R40 | To set biasing threshold for power flow controlling BJT. | Resistor fails-open. | BJT will be permanently turned OFF. Input power path will be broken. No output available at HV transformer board. | Redundant power to one of the iVSL driver board will be cut-off. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Over voltage. Over Temperature. Over stress due to shock or vibration. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant 24 V supply to iVSL Driver boards will be provided via UPSB. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 10 | [11 empty] | 5247
SV104 - 5248 |  |  |  | Resistor fails-short. | 24 V will be replicated at the emitter for the shorted duration, on-board ICs may get burn due to this over-voltage. BJT will eventually fail-open due to over-current. Input power path will be broken. No output available at HV transformer board. | Redundant power to one of the iVSL driver board will be cut-off. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Wear-out due to extensive use. Excessive humidity. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant 24 V supply to iVSL Driver boards will be provided via UPSB. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 10 | [11 empty] | 5248
SV104 - 5249 | Freewheeling Diode. |  | To provide reverser current flow path. | Diode fails-open. | No protection for BJT will be available. Reverse voltage development across BJT will damage it. No output available. | Redundant power to one of the iVSL driver board will be cut-off. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Mechanical stress or impact during assembly. Overcurrent. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant 24 V supply to iVSL Driver boards will be provided via UPSB. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 10 | [9 empty] | 0 |  | 5249
SV104 - 5250 |  |  |  | Diode fails-short. | Input will appear as it is on output which will damage PWM controller and gate driver ICs permanently. No output available. . | Redundant power to one of the iVSL driver board will be cut-off. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Large reverse voltage. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant 24 V supply to iVSL Driver boards will be provided via UPSB. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 10 | [11 empty] | 5250
SV104 - 5251 | 15 V Rail Output Side Capacitors. | C22,C19,C20 | To stable output voltage and to suppress ripples. | Capacitor fails-open. | No immediate effect on board.. | If no other failure is observed on the board, iVSL driver board will stay powered. Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | Mechanical stress. Localized heating for long time will separate end connection of capacitor. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant 24 V supply to iVSL Driver boards will be provided via UPSB. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [11 empty] | 5251
SV104 - 5252 |  |  |  | Capacitor fails-short. | 15 V power supply will be shorted to ground. On-board electronics will not be powered up. No output available at HV transformer board. | Redundant power to one of the iVSL driver board will be cut-off. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Wear-out due to dielectric degradation. High-voltage transients. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant 24 V supply to iVSL Driver boards will be provided via UPSB. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 10 | [11 empty] | 5252
SV104 - 5253 | 24 V Feedback Signal Side Resistor. | R38 | To provide 24 V sensing feedback path. | Resistor fails-open. | 15 V regulator will keep on working from input side and will not turn off. Which will heat up the resistor on MOSFET Q6 drain and will burn out eventually. No output available at HV transformer board. . | Redundant power to one of the iVSL driver board will be cut-off. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Over voltage. Over Temperature. Over stress due to shock or vibration. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant 24 V supply to iVSL Driver boards will be provided via UPSB. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 10 | [11 empty] | 5253
SV104 - 5254 |  |  |  | Resistor fails-short. | Over-current will cause the resistor to eventually fail-open. 15 V regulator will keep on working from input side and will not turn off. Which will heat up the resistor on MOSFET Q6 drain and will burn out eventually. No output available at HV transformer board. | Redundant power to one of the iVSL driver board will be cut-off. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Wear-out due to extensive use. Excessive humidity. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant 24 V supply to iVSL Driver boards will be provided via UPSB. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 10 | [9 empty] | 0 |  | 5254
SV104 - 5255 | 24 V Feedback Signal Side 9 V Zener Diode. | D23 | To maintain a constant 9 V drop. To turn off the startup circuitry once full bridge auxiliary supply exceeds 9.1 V. | Diode fails-open. | 15 V regulator will keep on working from input side and will not turn off. Which will heat up the resistor on MOSFET Q6 drain and will burn out eventually. No output available at HV transformer board. | Redundant power to one of the iVSL driver board will be cut-off. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Mechanical stress or impact during assembly. Overcurrent. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant 24 V supply to iVSL Driver boards will be provided via UPSB. | 2 | 4 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 20 | [9 empty] | 0 |  | 5255
SV104 - 5256 |  |  |  | Diode fails-short. | Startup circuitry will be turned off before full bridge secondary is activated completely. As a result startup circuitry will keep activating and then turn off due to aux voltage. This will eventually damage the startup circuitry of board. No output available at HV transformer board. | Redundant power to one of the iVSL driver board will be cut-off. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Excessive Temperature. Overcurrent. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant 24 V supply to iVSL Driver boards will be provided via UPSB. | 2 | 4 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 20 | [9 empty] | 0 |  | 5256
SV104 - 6764 | 24 V Feedback Signal Side - R39 | R39 | Voltage divider resistor-Low side | Resistor fails-open | 15 V regulator will keep on working from input side and will not turn off. Which will heat up the resistor on MOSFET Q6 drain and will burn out eventually. No output available at HV transformer board. | Redundant power to one of the iVSL driver board will be cut-off. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Over voltage. Over Temperature. Over stress due to shock or vibration. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant 24 V supply to iVSL Driver boards will be provided via UPSB. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 10 | [9 empty] | 0 |  | 6764
SV104 - 6765 |  |  |  | Resistor fails-short | 15 V regulator will keep on working from input side and will not turn off. Which will heat up the resistor on MOSFET Q6 drain and will burn out eventually. No output available at HV transformer board. | Redundant power to one of the iVSL driver board will be cut-off. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Wear-out due to extensive use. Excessive humidity. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant 24 V supply to iVSL Driver boards will be provided via UPSB. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 10 | [11 empty] | 6765
SV104 - 6766 | 24 V Feedback Signal Side - D23 | D23 | To maintain a constant 9 V drop. To turn off the startup circuitry once full bridge auxiliary supply exceeds 9.1 V. | Diode fails-open | 15 V regulator will keep on working from input side and will not turn off. Which will heat up the resistor on MOSFET Q6 drain and will burn out eventually. No output available at HV transformer board. | Redundant power to one of the iVSL driver board will be cut-off. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Excessive forward current flow. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant 24 V supply to iVSL Driver boards will be provided via UPSB. | 2 | 4 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 20 | [9 empty] | 0 |  | 6766
SV104 - 6767 |  |  |  | Diode fails-short | No immediate effect on board. | If no other failure is observed on the board, iVSL driver board will stay powered. Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | Large reverse voltage. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant 24 V supply to iVSL Driver boards will be provided via UPSB. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [11 empty] | 6767
SV104 - 6768 | 24 V Feedback Signal Side - D24 | D24 | To prevent reverse power flow from startup circuitry | Diode fails-open | As soon as auxiliary will develop board will be disabled and power-up again and this cycle will keep repeating which will damage the startup circuitry permanently. No output available at HV transformer board. | Redundant power to one of the iVSL driver board will be cut-off. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Excessive forward current flow. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant 24 V supply to iVSL Driver boards will be provided via UPSB. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 10 | [9 empty] | 0 |  | 6768
SV104 - 6769 |  |  |  | Diode fails-short | Startup circuitry will disable itself before powering up the board. It will happen repeatedly eventually damaging the startup circuitry. No output available at HV transformer board. | Redundant power to one of the iVSL driver board will be cut-off. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Large reverse voltage. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant 24 V supply to iVSL Driver boards will be provided via UPSB. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 10 | [11 empty] | 6769
SV104 - 6770 | 24 V Feedback Signal Side - D26 | D26 | Overvoltage protection for MOSFET | Diode fails-open | No immediate effect on board. | If no other failure is observed on the board, iVSL driver board will stay powered. Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | Excessive forward current flow. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant 24 V supply to iVSL Driver boards will be provided via UPSB. | 2 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 10 | [9 empty] | 0 |  | 6770
SV104 - 6771 |  |  |  | Diode fails-short | 15 V regulator will keep on working from input side and will not turn off. Which will heat up the resistor on MOSFET Q6 drain and will burn out eventually. No output available at HV transformer board. | Redundant power to one of the iVSL driver board will be cut-off. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Large reverse voltage. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant 24 V supply to iVSL Driver boards will be provided via UPSB. | 2 | 4 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 20 | [11 empty] | 6771
SV104 - 5257 | 24 V Feedback Signal Side MOSFET. | Q7 | To turn OFF power flow controlling MOSFET when auxiliary voltage develops. | MOSFET fails-open. | 15 V regulator will keep on working from input side and will not turn off. Which will heat up the resistor on MOSFET Q6 drain and will burn out eventually. No output available at HV transformer board. | Redundant power to one of the iVSL driver board will be cut-off. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Overheating Mechanical stress resulting in cracked MOSFET body. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant 24 V supply to iVSL Driver boards will be provided via UPSB. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 10 | [11 empty] | 5257
SV104 - 5258 |  |  |  | MOSFET fails-short. | Startup circuitry will remain off permanently as Q6 remains off permanently. 15 V regulator will keep on working from input side and will not turn off. Which will heat up the resistor on MOSFET Q6 drain and will burn out eventually. No output available at HV transformer board. | Redundant power to one of the iVSL driver board will be cut-off. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Transients Overheating as a result of loose connection with heat sink Overcurrent Counterfeit part Damage during mechanical assembly of board Metallic debris stuck in between terminals | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant 24 V supply to iVSL Driver boards will be provided via UPSB. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 10 | [11 empty] | 5258
SV104 - 5259 | 24 V Feedback Signal Side MOSFET.- Zener at Gate | D25 | To protect MOSFET (Q6) gate from over-voltage. | Diode fails-open. | Over-voltage protection of MOSFET won't be available. No immediate effect on board in normal operations. | If no other failure is observed on the board, iVSL driver board will stay powered. Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | Mechanical stress or impact during assembly. Overcurrent. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant 24 V supply to iVSL Driver boards will be provided via UPSB. | 2 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 10 | [9 empty] | 0 |  | 5259
SV104 - 5260 |  |  |  | Diode fails-short. | Board will not power up as startup circuit will remain off. Q6 will remain permanently off. No output available at HV transformer board. | Redundant power to one of the iVSL driver board will be cut-off. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Large reverse voltage. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant 24 V supply to iVSL Driver boards will be provided via UPSB. | 2 | 4 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 20 | [11 empty] | 5260
| PWM Controller | [26 empty] | 0
SV104 - 5261 | PWM Controller IC. | U1 | To provide alternate PWM pulses for full bridge gate driver. | IC output is permanently low. | No PWM will be available for half bridge driver ICs, No output available at HV transformer board. Redundant power to one of the iVSL driver board will be cut-off. | Redundant power to one of the iVSL driver board will be cut-off. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Electrical Overstress. ESD. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 10 | [11 empty] | 5261
SV104 - 5262 |  |  |  | One of output is permanently high. | Output of Full Bridge circuit will be 12 V at no load. HV transformer board will have no output as soon as load is applied. Redundant power to one of the iVSL driver board will be cut-off. | Redundant power to one of the iVSL driver board will be cut-off. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Electrical Overstress. ESD. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 10 | [11 empty] | 5262
SV104 - 5263 |  |  |  | PWM is having different duty cycle than desired. | Output of Full Bridge circuit will have different duty cycle. HV transformer board will have more or less than 24 V output. | If no other failure is observed on the board, iVSL driver board will stay powered. Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | Internal IC damage. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 2 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 10 | [11 empty] | 5263
SV104 - 5264 | Line Under-Voltage Lockout Voltage Divider High Side Resistor. | R1 | To turn OFF gate driver PWM in case of under-voltage. | Resistor fails-open. | PWM controller will remain off permanently. No output available. | Redundant power to one of the iVSL driver board will be cut-off. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Over voltage. Over Temperature. Over stress due to shock or vibration. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 10 | [9 empty] | 0 |  | 5264
SV104 - 5265 |  |  |  | Resistor fails-short. | UVLO pin will get damaged, No PWM will be available for half bridge driver ICs, No output available at HV transformer board. Redundant power to one of the iVSL driver board will be cut-off. | Redundant power to one of the iVSL driver board will be cut-off. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Wear-out due to extensive use. Excessive humidity. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 10 | [11 empty] | 5265
SV104 - 5266 | Line Under-Voltage Lockout Voltage Divider Low Side Resistor. | R13 | To turn OFF gate driver PWM in case of under-voltage. | Resistor fails-open. | UVLO pin will get damaged, No PWM will be available for half bridge driver ICs, No output available at HV transformer board. Redundant power to iSCR driver board will be cut-off. | Redundant power to one of the iVSL driver board will be cut-off. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Over voltage. Over Temperature. Over stress due to shock or vibration. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 10 | [9 empty] | 0 |  | 5266
SV104 - 5267 |  |  |  | Resistor fails-short. | PWM controller will remain off permanently. No output available. | Redundant power to one of the iVSL driver board will be cut-off. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Wear-out due to extensive use. Excessive humidity. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 10 | [11 empty] | 5267
SV104 - 5268 | RT2 Biasing Resistor. | R14 | To control oscillator dead time. | Resistor fails-open. | Dead time between alternating PWMs will be altered (maximum). 1 PWM will be permanently high, while other will be permanently low. Output of isolation transformer will not be available. No output available at HV transformer board. Redundant power to one of the iVSL driver board will be cut-off. | Redundant power to one of the iVSL driver board will be cut-off. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Over voltage. Over Temperature. Over stress due to shock or vibration. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 10 | [11 empty] | 5268
SV104 - 5269 |  |  |  | Resistor fails-short. | Dead time between alternating PWMs will be altered (maximum). 1 PWM will be permanently high, while other will be permanently low. Output of isolation transformer will not be available. No output available at HV transformer board. Redundant power to one of the iVSL driver board will be cut-off. | Redundant power to one of the iVSL driver board will be cut-off. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Wear-out due to extensive use. Excessive humidity. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 10 | [9 empty] | 0 |  | 5269
SV104 - 5270 | RT1 Biasing Resistor. | R15 | To control oscillator maximum ON time. | Resistor fails-open. | Dead time between alternating PWMs will be altered (maximum). 1 PWM will be permanently high, while other will be permanently low. Output of isolation transformer will not be available. No output available at HV transformer board. Redundant power to one of the iVSL driver board will be cut-off. | Redundant power to one of the iVSL driver board will be cut-off. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Over voltage. Over Temperature. Over stress due to shock or vibration. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 10 | [11 empty] | 5270
SV104 - 5271 |  |  |  | Resistor fails-short. | Dead time between alternating PWMs will be altered (maximum). 1 PWM will be permanently high, while other will be permanently low. Output of isolation transformer will not be available. No output available at HV transformer board. Redundant power to one of the iVSL driver board will be cut-off. | Redundant power to one of the iVSL driver board will be cut-off. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Wear-out due to extensive use. Excessive humidity. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 10 | [11 empty] | 5271
SV104 - 5272 | Restart Timer Resistor. | R16 | To set PWM restart signal biasing. | Resistor fails-open. | Restart timer functionality will be compromised. No immediate effect on board in normal operations. | If no other failure is observed on the board, iVSL driver board will stay powered. Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | Over voltage. Over Temperature. Over stress due to shock or vibration. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [11 empty] | 5272
SV104 - 5273 |  |  |  | Resistor fails-short. | Restart timer functionality will be compromised. No immediate effect on board in normal operations. | If no other failure is observed on the board, iVSL driver board will stay powered. Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | Wear-out due to extensive use. Excessive humidity. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [11 empty] | 5273
SV104 - 5274 | Soft-Start Capacitor. | C10 | To provide soft-start biasing value. | Capacitor fails-open. | No soft start will be implemented. No immediate effect on board in normal operations. | If no other failure is observed on the board, iVSL driver board will stay powered. Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | Mechanical stress. Localized heating for long time will separate end connection of capacitor. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [11 empty] | 5274
SV104 - 5275 |  |  |  | Capacitor fails-short. | PWM controller will turn off permanently. No output available for board. | Redundant power to one of the iVSL driver board will be cut-off. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Wear-out due to dielectric degradation. High-voltage transients. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 10 | [9 empty] | 0 |  | 5275
SV104 - 5276 | Ramp Control Resistor. | R12 | To provide ramp control of PWM. | Resistor fails-open. | PWM ramp will be affected. Output of Full Bridge circuit will be different than desired. HV transformer board will have more or less than 24 V output. | If no other failure is observed on the board, iVSL driver board will stay powered. Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | Over voltage. Over Temperature. Over stress due to shock or vibration. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [11 empty] | 5276
SV104 - 5277 |  |  |  | Resistor fails-short. | PWM ramp will be affected. Output of Full Bridge circuit will be different than desired. HV transformer board will have more or less than 24 V output. | If no other failure is observed on the board, iVSL driver board will stay powered. Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | Wear-out due to extensive use. Excessive humidity. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [9 empty] | 0 |  | 5277
SV104 - 5278 | Current Sense Signal Filtration Capacitor. | C12 | To filter the CS signal. | Capacitor fails-open. | No immediate effect. | If no other failure is observed on the board, iVSL driver board will stay powered. Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | Mechanical stress. Localized heating for long time will separate end connection of capacitor. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [11 empty] | 5278
SV104 - 5279 |  |  |  | Capacitor fails-short. | Capacitor will fail-open due to over-current. PWM current limiting functionality will be compromised while the capacitor remains shorted. No immediate effect on board in normal operations. | If no other failure is observed on the board, iVSL driver board will stay powered. Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | Wear-out due to dielectric degradation. High-voltage transients. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [11 empty] | 5279
SV104 - 5280 | Current Sense Capacitor. | C9 | To limit PWM current. | Capacitor fails-open. | PWM current limiting functionality will be compromised. No immediate effect on board in normal operations. | If no other failure is observed on the board, iVSL driver board will stay powered. Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | Mechanical stress. Localized heating for long time will separate end connection of capacitor. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [11 empty] | 5280
SV104 - 5281 |  |  |  | Capacitor fails-short. | PWM current limiting functionality will be compromised. No immediate effect on board in normal operations. | If no other failure is observed on the board, iVSL driver board will stay powered. Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | Wear-out due to dielectric degradation. High-voltage transients. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [11 empty] | 5281
SV104-12385 | Decoupling Capacitor | C11 | To Filter Noise | Capacitor fails-open. | No immediate effect on board in normal operations. | If no other failure is observed on the board, iVSL driver board will stay powered. Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | Mechanical stress. Localized heating for long time will separate end connection of capacitor. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. Vibration Testing. | None. | 5 | 5 | [11 empty] | 12385
SV104-12386 |  |  |  | Capacitor fails-short. | Internal Reference Voltage will be shorted to ground. PWM output will be disabled. Input Fuse Will be Blown No output available at HV transformer board. | Redundant power to one of the iVSL driver board will be cut-off. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Wear-out due to dielectric degradation. High-voltage transients. De-gradation of components. Water ingress during humidity condition as it is film capacitor. Overvoltage | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. Environmental Testing. | None. | 5 | 10 | [9 empty] | 0 |  | 12386
SV104-10947 | Input Filtration Capacitance | C1 | To suppress ripples on input voltage. | Capacitor fails-open. | No immediate effect on board due to presence of multiple capacitors at different stages.. | If no other failure is observed on the board, iVSL driver board will stay powered. Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | Mechanical stress. Localized heating for long time will separate end connection of capacitor. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. Vibration Testing. | None. | 5 | 5 | [11 empty] | 10947
SV104-10948 |  |  |  | Capacitor fails-short. | 15V rail will get shorted to ground thus No output available at HV transformer board . | Redundant power to one of the iVSL driver board will be cut-off. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Wear-out due to dielectric degradation. High-voltage transients. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 10 | [9 empty] | 0 |  | 10948
SV104-10949 | Current Sense Resistance | R28 | To Sense Overcurrent | Resistor fails-open. | Overcurrent Protection will be compromised during overcurrent condition at primary. No immediate Effect in normal condition. | If no other failure is observed on the board, iVSL driver board will stay powered. Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | Over voltage. Over Temperature. Over stress due to shock or vibration. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [11 empty] | 10949
SV104-10950 |  |  |  | Resistor fails-short. | IC may trigger False overcurrent and disable output. No output available at HV transformer board | Redundant power to one of the iVSL driver board will be cut-off. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Wear-out due to extensive use. Excessive humidity. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 10 | [9 empty] | 0 |  | 10950
SV104 - 5282 | Output Driver Resistor. | R4,R5 | To limit gate driver current. | Resistor fails-open. | Gate driver PWM path will be broken. No output available at HV transformer board. Redundant power to one of the iVSL driver board will be cut-off. | Redundant power to one of the iVSL driver board will be cut-off. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Over voltage. Over Temperature. Over stress due to shock or vibration. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 10 | [11 empty] | 5282
SV104 - 5283 |  |  |  | Resistor fails-short. | No immediate till the shorted duration. Resistor will fail-open due to over-current. Gate driver PWM path will be broken. No output available at HV transformer board. Redundant power to one of the iVSL driver board will be cut-off. | Redundant power to one of the iVSL driver board will be cut-off. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Wear-out due to extensive use. Excessive humidity. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 10 | [9 empty] | 0 |  | 5283
| Full Bridge Circuit | [26 empty] | 0
SV104 - 5284 | Half Bridge Gate Driver IC. | U2, U3 | To provide gate driver signal for half bridge MOSFETs. | Both output are permanently low. | One half bridge section will not have output. Output of Full Bridge circuit will be 12 V at no load. HV transformer board will have no output as soon as load is applied. Redundant power to one of the iVSL driver board will be cut-off. | Redundant power to one of the iVSL driver board will be cut-off. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Electrical Overstress (Overvoltage). ESD. Counterfeit part. Stress or impact during assembly. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 10 | [11 empty] | 5284
SV104 - 8899 |  |  |  | High side output is permanently low. | Full bridge functionality will be disturbed. No output will be available at HV transformer board as soon as load is applied. Redundant power to one of the iVSL driver board will be cut-off. | Redundant power to one of the iVSL driver board will be cut-off. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Electrical Overstress (Overvoltage). ESD. Counterfeit part. Stress or impact during assembly. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 10 | [11 empty] | 8899
SV104 - 5285 |  |  |  | High side output is permanently high. | One MOSFET will be permanently turned ON. During times, when low side MOSFET of same half bridge will turn ON, HV DC line get shorted will ground. Due to high current flow, power MOSFETs may get damaged. Input side fuse will burn out and prevent cascading failures. Redundant power to one of the iVSL driver board will be cut-off. | Redundant power to one of the iVSL driver board will be cut-off. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Electrical Overstress (Overvoltage). ESD. Counterfeit part. Stress or impact during assembly. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 10 | [11 empty] | 5285
SV104 - 8900 | Half Bridge Gate Driver IC. | U2, U3 | To provide gate driver signal for half bridge MOSFETs. | Low side output is permanently low. | Full bridge functionality will be disturbed. No output will be available at HV transformer board as soon as load is applied. Redundant power to one of the iVSL driver board will be cut-off. | Redundant power to one of the iVSL driver board will be cut-off. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Electrical Overstress (Overvoltage). ESD. Counterfeit part. Stress or impact during assembly. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 10 | [11 empty] | 8900
SV104 - 8901 |  |  |  | Low side output is permanently high. | During times, when high side MOSFET of same half bridge will turn ON, HV DC line get shorted with ground. Due to high current flow, power MOSFETs may get damaged. Input side fuse will burn out and prevent cascading failures. Redundant power to one of the iVSL driver board will be cut-off. | Redundant power to one of the iVSL driver board will be cut-off. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Electrical Overstress (Overvoltage). ESD. Counterfeit part. Stress or impact during assembly. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 10 | [9 empty] | 0 |  | 8901
SV104 - 5286 |  |  |  | Both outputs are permanently high. | Both MOSFETs will be permanently turned ON. HV DC line will get shorted with ground. Due to high current flow, power MOSFETs may get damaged. Input side fuse will burn out and prevent cascading failures. Redundant power to one of the iVSL driver board will be cut-off. | Redundant power to one of the iVSL driver board will be cut-off. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Electrical Overstress (Overvoltage). ESD. Counterfeit part. Stress or impact during assembly. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 10 | [11 empty] | 5286
SV104 - 5287 | Half Bridge Gate Driver IC - Filter Capacitor. | C4,C5 | To provide high side gate driver floating supply. | Capacitor fails-open. | Output of gate driver IC will be affected. No output available at HV transformer board. Redundant power to one of the iVSL driver board will be cut-off. | Redundant power to one of the iVSL driver board will be cut-off. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Mechanical stress. Localized heating for long time will separate end connection of capacitor. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 10 | [9 empty] | 0 |  | 5287
SV104 - 5288 |  |  |  | Capacitor fails-short. | Output of gate driver IC will be affected. No output available at HV transformer board. Redundant power to one of the iVSL driver board will be cut-off. | Redundant power to one of the iVSL driver board will be cut-off. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Wear-out due to dielectric degradation. High-voltage transients. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 10 | [11 empty] | 5288
SV104 - 5289 | Gate Driver Output Circuit - Resistor. | R7,R24,R6,R23 | To provide path between gate driver IC and gate. | Resistor fails-open. | Output path of gate driver IC will be broken for one MOSFET. Distorted square wave will be available at full bridge circuit output. HV transformer board will have lesser output than desired. | Redundant power to one of the iVSL driver board will be cut-off. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Over voltage. Over Temperature. Over stress due to shock or vibration. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 10 | [9 empty] | 0 |  | 5289
SV104 - 5290 |  |  |  | Resistor fails-short. | Over-current will cause the resistor to eventually fail-open. Output path of gate driver IC will be broken for one MOSFET. Distorted square wave will be available at full bridge circuit output. HV transformer board will have lesser output than desired. | Redundant power to one of the iVSL driver board will be cut-off. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Wear-out due to extensive use. Excessive humidity. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 10 | [11 empty] | 5290
SV104 - 5291 | Gate Driver Output Circuit - General Purpose Diode. | D1,D2,D3,D4 | To turn off the MOSFET quickly through low resistance path at gate. | Diode fails-open. | MOSFET will turn off through larger resistor which will result in increased switching losses. No immediate effect in case of normal operations. | If no other failure is observed on the board, iVSL driver board will stay powered. Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | Mechanical stress or impact during assembly. Overcurrent. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [9 empty] | 0 |  | 5291
SV104 - 5292 |  |  |  | Diode fail-short. | Over-current will cause the diode to eventually fail-open. MOSFET will turn off through larger resistor which will result in increased switching losses. No immediate effect in case of normal operations. | If no other failure is observed on the board, iVSL driver board will stay powered. Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | Large reverse voltage. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [11 empty] | 5292
SV104-10951 | Gate Driver Output Circuit -Discharge Resistor. | R2,R3,R20,R21 | To provide low resistance path between gate driver IC and gate to discharge miller capacitance. | Resistor fails-open. | Gate Capacitance will discharge slowly through high resistance path thus on/off time will be disturbed Switching losses will increase. No immediate effect ion board. | If no other failure is observed on the board, iVSL driver board will stay powered. Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | Over voltage. Over Temperature. Over stress due to shock or vibration. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [11 empty] | 10951
SV104-10952 |  |  |  | Resistor fails-short. | Switching losses will increase. No immediate effect on board. | If no other failure is observed on the board, iVSL driver board will stay powered. Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | Wear-out due to extensive use. Excessive humidity. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [9 empty] | 0 |  | 10952
SV104-10953 | MOSFET resistance for Miller Capacitance | R10,R27,R11,R26 | To discharge capacitance between all terminals of MOSFET | Resistor fails-open | Abnormal Behavior of MOSFET Might turn ON/OFF abnormally and can damage board. No output available at HV transformer board | Redundant power to one of the iVSL driver board will be cut-off. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Over voltage. Over Temperature. Over stress due to shock or vibration. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. Vibration testing. | None. | 5 | 10 | [11 empty] | 10953
SV104-10954 |  |  |  | Resistor fails-short | Gate and Source of MOSFET will have no voltage difference so MOSFET cannot operate No output available at HV transformer board | Redundant power to one of the iVSL driver board will be cut-off. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Wear-out due to extensive use. Excessive humidity. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. Vibration testing. | None. | 5 | 10 | [9 empty] | 0 |  | 10954
SV104-10955 | Half Bridge Gate Driver IC - High Side Supply Capacitor. | C7,C15,C16,C8 | To provide high side supply and to ensure bootstrapping in order to operate MOSFET. | One Capacitor fails-open. | No immediate effect as the parallel capacitor will be available and will make sure that MOSFET works properly | If no other failure is observed on the board, iVSL driver board will stay powered. Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | Mechanical stress. Localized heating for long time will separate end connection of capacitor. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [11 empty] | 10955
SV104-10956 |  |  |  | Both Capacitors fails-open. | MOSFET Cannot operate properly No output available at HV transformer board | Redundant power to one of the iVSL driver board will be cut-off. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Mechanical stress. Localized heating for long time will separate end connection of capacitor. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 10 | [11 empty] | 10956
SV104-10957 |  |  |  | Capacitor fails-short. | MOSFET Cannot operate properly IC may get damaged No output available at HV transformer board | Redundant power to one of the iVSL driver board will be cut-off. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Wear-out due to dielectric degradation. High-voltage transients. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 10 | [9 empty] | 0 |  | 10957
SV104 - 5293 | Full Bridge Circuit - MOSFET | Q1,Q2,Q3,Q4 | To convert HV DC to HV AC signal. | MOSFET fails-open. | Distorted square wave will be available at full bridge circuit output. HV transformer board will have lesser output than desired. | Redundant power to one of the iVSL driver board will be cut-off. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Overheating Mechanical stress resulting in cracked MOSFET body. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 10 | [11 empty] | 5293
SV104 - 5294 |  |  |  | MOSFET fails-short. | No voltage will be available at transformer output, for the shorted duration. No output available at HV transformer board. Redundant power to one of the iVSL driver board will be cut-off. | Redundant power to one of the iVSL driver board will be cut-off. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Transients Overheating as a result of loose connection with heat sink Overcurrent Counterfeit part Damage during mechanical assembly of board Metallic debris stuck in between terminals | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 10 | [11 empty] | 5294
SV104-10958 | Gate Driver Output Circuit -Pull Down resistance. | R29,R8 | To provide current sense signal to controller | One Resistor fails-open. | Current over limit value will decrease down to half. No immediate affect in normal condition but in case of overloaded condition current limit will be activated early. | If no other failure is observed on the board, iVSL driver board will stay powered. Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | Over voltage. Over Temperature. Over stress due to shock or vibration. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [11 empty] | 10958
SV104-10959 |  |  |  | Both Resistor fails-open. | Full bridge circuit ground connection will be disconnected No output available at HV transformer board | Redundant power to one of the iVSL driver board will be cut-off. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Over voltage. Over Temperature. Over stress due to shock or vibration. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 10 | [9 empty] | 0 |  | 10959
SV104-10960 |  |  |  | Resistor fails-short. | No immediate effect in case of normal operations. Overcurrent protection will not be available. | If no other failure is observed on the board, iVSL driver board will stay powered. Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | Wear-out due to extensive use. Excessive humidity. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [11 empty] | 10960
SV104 - 5295 | HV Isolation Transformer | P113720 | To step down 400 V AC to 24 V AC. | Primary winding fails-open. | No voltage will be available at transformer output. No output available at HV transformer board. Redundant power to one of the iVSL driver board will be cut-off. | Redundant power to one of the iVSL driver board will be cut-off. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | High operating temperature. Overloading. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 10 | [11 empty] | 5295
SV104 - 5296 |  |  |  | Secondary winding fails-open. | No output available. Redundant power to one of the iVSL driver board will be cut-off. | Redundant power to one of the iVSL driver board will be cut-off. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | High operating temperature. Overloading. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 10 | [11 empty] | 5296
SV104 - 5297 |  |  |  | Core degradation. | Output voltage will be less than desired value. | Redundant power to one of the iVSL driver board will be cut-off. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Mechanical Stress | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 10 | [11 empty] | 5297
SV104 - 5298 |  |  |  | Winding insulation melting. | Turn ratio of transformer will be affected. Output voltage will be less than desired value. | Redundant power to one of the iVSL driver board will be cut-off. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Over voltage. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 10 | [9 empty] | 0 |  | 5298
SV104 - 6772 |  |  |  | Isolation Failure. | If failure is such that board cannot provide any level of isolation then it will damage iVSL driver board. iVSL driver board will not be powered up. | In case of complete isolation failure, one of the VSLs will not be able to open. Device will stay in monitoring mode. | Affected device and associated group will not be able to enter injection mode. System will keep working normally with reduced injection capability. | 4 | Temperature cycling. Manufacturing Deficiency. Vibration. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 4 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 20 | [11 empty] | 6772
SV104 - 6773 |  |  |  | Auxiliary winding failure(Open) | No auxiliary voltage will be available. Startup circuit will not shutdown eventually burning out. No output will be available for HV-ISO board | Redundant power to one of the iVSL driver board will be cut-off. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Over voltage. Overheating. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 10 | [11 empty] | 6773
SV104 - 6774 |  |  |  | Post insulator fails | Insulator failure will not have impact during normal condition as it is to prevent early partial discharge during humid condition. This will not impact bypass side board in any condition but will be critical for MVAR side board in condensed humidity condition. If failure is such that board cannot provide any level of isolation then it will damage iVSL driver board. iVSL driver board will not be powered up. | In case of complete isolation failure, one of the VSLs will not be able to open. Device will stay in monitoring mode. | Affected device and associated group will not be able to enter injection mode. System will keep working normally with reduced injection capability. | 4 | Corrosion. Manufacturing Deficiency. Vibration. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 4 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 20 | [11 empty] | 6774
SV104 - 6775 |  |  |  | Potting crack or physical damage | Partial discharge will start resulting in degradation of isolation barrier with the time. No immediate effect as isolation of even 400 Vrms will be enough for normal operation of iVSL driver board. | If no other failure is observed on the board, iVSL driver board will stay powered. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Temperature variations. Manufacturing Deficiency. Vibration. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 10 | [9 empty] | 0 |  | 6775
SV104 - 5299 | HV Isolation Transformer - output Side Full Rectifier - Diode | D5,D6,D8 | To convert 24 V AC to 24 V DC. | Diode fails-open. | Output cut to half if half side is working. Redundant power to one of the iVSL driver board will be cut-off. | If no other failure is observed on the board, iVSL driver board will stay powered. Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | Excessive forward current flow. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [9 empty] | 0 |  | 5299
SV104 - 5300 |  |  |  | Diode fails-short. | Secondary winding will get shorted if any diode fails-short. As a result of shortage, excessive amount of current will flow damaging two diodes permanently. Diodes will eventually get open and no output will be available Redundant power to one of the iVSL driver board will be cut-off. | Redundant power to one of the iVSL driver board will be cut-off. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Large reverse voltage. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 10 | [11 empty] | 5300
SV104-10961 | Output Side Capacitor. | C13,C14 | To suppress output side ripples and to provide filtration. | Capacitor fails-open. | Output voltage may have ripples. No immediate effect on HV transformer board output. | If no other failure is observed on the board, iVSL driver board will stay powered. Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | Mechanical stress. Localized heating for long time will separate end connection of capacitor. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [11 empty] | 10961
SV104-10962 |  |  |  | Capacitor fails-short. | No voltage available at the output for the shorted duration. Redundant power to one of the iVSL driver board will be cut-off. | Redundant power to one of the iVSL driver board will be cut-off. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Wear-out due to dielectric degradation. High-voltage transients. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 10 | [11 empty] | 10962
SV104 - 5301 | HV Isolation Transformer - Feedback Side Full Rectifier - Diode | D15,D16,D19,D20 | To convert 24 V AC to 24 V DC for feedback. | Diode fails-open. | Output cut to half if half side is working. Redundant power supply to VSL board will be cut off. | Redundant power to one of the iVSL driver board will be cut-off. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Excessive forward current flow. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 10 | [11 empty] | 5301
SV104 - 5302 |  |  |  | Diode fails-short. | Auxiliary winding will get shorted if any diode fails-short. As a result of shortage, excessive amount of current will flow damaging two diodes permanently. Diodes will eventually get open and no output will be available. Redundant power supply to VSL board will be cut off. | Redundant power to one of the iVSL driver board will be cut-off. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Large reverse voltage. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 10 | [9 empty] | 0 |  | 5302
SV104 - 5303 | Output Side Capacitor. | C17,C18 | To suppress output side ripples and to provide filtration. | Capacitor fails-open. | Output voltage may have ripples. No immediate effect on HV transformer board output. | If no other failure is observed on the board, iVSL driver board will stay powered. Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | Mechanical stress. Localized heating for long time will separate end connection of capacitor. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [9 empty] | 0 |  | 5303
SV104 - 5304 |  |  |  | Capacitor fails-short. | No voltage available at the output for the shorted duration. Redundant power to one of the iVSL driver board will be cut-off. | Redundant power to one of the iVSL driver board will be cut-off. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Wear-out due to dielectric degradation. High-voltage transients. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 10 | [11 empty] | 5304
SV104-10963 | Current Limiting resistance for LED (D9) | R44 | To limit current through the LED (D9) | Resistor fails-open | LED indication functionality will be compromised No immediate effect on HV transformer board output. | If no other failure is observed on the board, iVSL driver board will stay powered. Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | Over voltage. Over Temperature. Over stress due to shock or vibration. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. Vibration testing. | None. | 5 | 5 | [9 empty] | 0 |  | 10963
SV104-10964 |  |  |  | Resistor fails-short | LED indication functionality will be compromised No immediate effect on HV transformer board output. | If no other failure is observed on the board, iVSL driver board will stay powered. Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | Wear-out due to extensive use. Excessive humidity. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. Vibration testing. | None. | 5 | 5 | [11 empty] | 10964
SV104-10965 | LED for status indication of voltage produced | D9 | Visual indication for board output status | Diode fails-open. | LED indication functionality will be compromised No immediate effect on HV transformer board output. | If no other failure is observed on the board, iVSL driver board will stay powered. Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | Over voltage. Over Temperature. Over stress due to shock or vibration. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. Vibration testing. | None. | 5 | 5 | [11 empty] | 10965
SV104-10966 |  |  |  | Diode fails-short | LED indication functionality will be compromised No immediate effect on HV transformer board output. | If no other failure is observed on the board, iVSL driver board will stay powered. Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | Wear-out due to extensive use. Excessive humidity. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. Vibration testing. | None. | 5 | 5 | [11 empty] | 10966
SV104-10967 | Load at output | R42,R43 | To keep open load voltage within a range | Resistor fails-open | No immediate effect on board. | If no other failure is observed on the board, iVSL driver board will stay powered. Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | Over voltage. Over Temperature. Over stress due to shock or vibration. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. Vibration testing. | None. | 5 | 5 | [11 empty] | 10967
SV104-10968 |  |  |  | Resistor fails-short | 24V supply will be shorted out to ground. Resistance will eventually fail open due to over current. No output available at HV transformer board | Redundant power to one of the iVSL driver board will be cut-off. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Wear-out due to extensive use. Excessive humidity. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. Vibration testing. | None. | 5 | 10 | [11 empty] | 10968
SV104 - 5305 | Heat Sink | HS1,HS2,HS3,HS4,HS5,HS6,HS7,HS8. | To provide cooling functionality for power components. | Loose connection between heat sink and power component. | Affected component will face high temperature rise during nominal current operations. Power component may get damaged causing HV transformer board output voltage to drop. Redundant power to one of the iVSL driver board will be cut-off. | Redundant power to one of the iVSL driver board will be cut-off. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | External overstress. Mis-handling. Excessive temperature causing joint melts. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 10 | [11 empty] | 5305
SV104-11411 | Secondary Winding Connector | J2 | Secondary of transformer | Connector Disconnected by external Force. | Secondary winding will be opened. No output available at HV transformer board. | Redundant power to one of the iVSL driver board will be cut-off. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Open Connections due to vibrations, mis-handling or mechanical stress. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. Vibration Testing. | None. | 5 | 10 | [11 empty] | 11411
SV104-11412 |  |  |  | Connector Burned out | Due to sparking connector will heat up and eventually burnout No output available at HV transformer board. | Redundant power to one of the iVSL driver board will be cut-off. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Connection Loose or Sparking at terminals Open Connections due to vibrations, mis-handling or mechanical stress. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. Vibration Testing. | None. | 5 | 10 | [11 empty] | 11412
SV104-11413 | Low voltage DC output Connector | J4 | Output of HVT board | Connector Disconnected by external Force. | Output path will be broken. No output available at HV transformer board. | Redundant power to one of the iVSL driver board will be cut-off. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Open Connections due to vibrations, mis-handling or mechanical stress. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. Vibration Testing. | None. | 5 | 10 | [11 empty] | 11413
SV104-11414 |  |  |  | Connector Burned out | Due to sparking connector will heat up and eventually burnout Output path will be broken. No output available at HV transformer board. | Redundant power to one of the iVSL driver board will be cut-off. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Connection Loose or Sparking at terminals Open Connections due to vibrations, mis-handling or mechanical stress. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. Vibration Testing. | None. | 5 | 10 | [9 empty] | 0 |  | 11414
SV104-11415 | Auxiliary winding Connector | J6 | Auxiliary winding of transformer for 24AUX | Connector Disconnected by external Force. | 24AUX path will be broken. Startup circuitry will turn on permanently resulting in overheating and permanently damage to startup resistor. No output available once HV-ISO reboot. | Redundant power to one of the iVSL driver board will be cut-off. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Open Connections due to vibrations, mis-handling or mechanical stress. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. Vibration Testing. | None. | 5 | 10 | [11 empty] | 11415
SV104-11416 |  |  |  | Connector Burned out | Due to sparking connector will heat up and eventually burnout 24AUX path will be broken. Startup circuitry will turn on permanently resulting in overheating and permanently damage to startup resistor. No output available once HV-ISO reboot. | Redundant power to one of the iVSL driver board will be cut-off. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Connection Loose or Sparking at terminals Open Connections due to vibrations, mis-handling or mechanical stress. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. Vibration Testing. | None. | 5 | 10 | [11 empty] | 11416
SV104-11417 | Primary winding of transformer | J1,J5 | primary winding of transformer | Connector Disconnected by external Force. | No voltage will be available at transformer output. No output available at HV transformer board. | Redundant power to one of the iVSL driver board will be cut-off. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Open Connections due to vibrations, mis-handling or mechanical stress. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. Vibration Testing. | None. | 5 | 10 | [11 empty] | 11417
SV104-11418 |  |  |  | Connector Burned out | Due to sparking connector will heat up and eventually burnout No voltage will be available at transformer output. No output available at HV transformer board. | Redundant power to one of the iVSL driver board will be cut-off. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Connection Loose or Sparking at terminals Open Connections due to vibrations, mis-handling or mechanical stress. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. Vibration Testing. | None. | 5 | 10 | [9 empty] | 0 |  | 11418
SV104 - 6776 | Connector failure |  | To provide input supply | Connector disconnected by external force | No output available at HV transformer board. Redundant power to one of the iVSL driver board will be cut-off. | Redundant power to one of the iVSL driver board will be cut-off. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | External overstress. Mis-handling. Excessive temperature causing joint melts. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 10 | [11 empty] | 6776
SV104 - 6777 | Connector | J3 | Input connector | Connector shorted | PHT-DC board external capacitor will dump full energy in board. HV-ISO board's input traces will burn out. Board will be damaged permanently. | One of the VSLs will not be able to open. Device will stay in monitoring mode. | Affected device and associated group will not be able to enter injection mode. System will keep working normally with reduced injection capability. | 4 | Manufacturing Deficiency. Excessive temperature causing joint melts. Excessive humidity. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Conformal coating whole connector and mask only mating part of pins. | 1 | 4 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 20 | [11 empty] | 6777
| HV Transformer Board for iiDCE and Clamp Board | [26 empty] | 0
| 15 V On-Board Supply | [26 empty] | 0
SV104 - 5306 | Input Side TRIACs. | D13,D12 | Reverse polarity protection. | TRIAC fails-open. | No immediate effect. Parallel TRIAC available for alternate path. | If no other failure is observed on the board, Clamp and iiDCE board will stay powered. Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | On-board fault causing higher current flow. Excessive forward current. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [11 empty] | 5306
SV104 - 5307 |  |  |  | TRIAC fails-short. | Reverse polarity protection will be compromised during shortage. Board will keep working normally if input is provided with correct polarity. | If no other failure is observed on the board, Clamp and iiDCE board will stay powered. Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | Large reverse voltage. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [11 empty] | 5307
SV104 - 6778 |  |  |  | Both TRIACs fail-short. | Reverse polarity protection will be compromised. Board will keep working normally if input is provided with correct polarity. | If no other failure is observed on the board, Clamp and iiDCE board will stay powered. Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | Large reverse voltage. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [11 empty] | 6778
SV104 - 6779 |  |  |  | Both TRIACs fail-open. | Input path will be broken. No output available at HV transformer board. | Clamp board will be unable to get power. Device\s capability to clamp surges via clamp board will not be available. iiDCE will get power via redundant HVT board. Fault current handling via iiDCE and iSCR driver board will be available. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | On-board fault causing higher current flow. Excessive forward current. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | Clamp board feedback is available to iiDCE. | 1 | 2 | [11 empty] | 6779
SV104 - 5308 | Input Side Fuse. | F2 | To cut-off supply in case of over-current. | Fuse fails-open. | Input power path will be broken. No output available at HV transformer board. | Clamp board will be unable to get power. Device\s capability to clamp surges via clamp board will not be available. iiDCE will get power via redundant HVT board. Fault current handling via iiDCE and iSCR driver board will be available. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | On-board fault causing higher current flow. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | Clamp board feedback is available to iiDCE. | 1 | 2 | [11 empty] | 5308
SV104 - 5309 | Input Side Filter Capacitors. | C2,C23 | To suppress ripples on input voltage. | Capacitor fails-open. | Input supply ripples may cause distorted output supply. No immediate effect on board.. | If no other failure is observed on the board, Clamp and iiDCE board will stay powered. Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | Electrical, mechanical or environmental overstress. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [9 empty] | 0 |  | 5309
SV104 - 5310 |  |  |  | Capacitor fails-short. | PHT-DC Capacitor will dump full energy in HV-ISO board leaving it permanently damage (Trace damage). No output available at HV transformer board. | Clamp board will be unable to get power. Device\s capability to clamp surges via clamp board will not be available. iiDCE will get power via redundant HVT board. Fault current handling via iiDCE and iSCR driver board will be available. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Wear-out due to dielectric degradation. High-voltage transients. De-gradation of components. Water ingress during humidity condition as it is film capacitor. Overvoltage | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. RTV application on edges to stop water ingress. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. Environmental Testing. | Clamp board feedback is available to iiDCE. | 1 | 2 | [11 empty] | 5310
SV104 - 5311 | Low Voltage Detection Zener Diode. (D7, D11, D10) | D7,D10,D11 | To set under-voltage lockout threshold. | Diode fails-open. | No voltage will be available at power controlling MOSFET gate. On-board 15 V supply will not be available. No output available at HV transformer board. | Clamp board will be unable to get power. Device\s capability to clamp surges via clamp board will not be available. iiDCE will get power via redundant HVT board. Fault current handling via iiDCE and iSCR driver board will be available. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | On-board fault causing higher current flow. Excessive forward current. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 2 | 4 | HALT. Electrical Stress Testing. Thermal Stress Testing. | Clamp board feedback is available to iiDCE. | 1 | 4 | [9 empty] | 0 |  | 5311
SV104 - 5312 |  |  |  | Diode fails-short.. | The threshold for UVLO detection will decrease. Board will turn on before the set threshold of 320 V. Slight effect will be on PHT-DC bus during low line current condition as it will ramp up slowly. Board will keep working. | If no other failure is observed on the board, Clamp and iiDCE board will stay powered. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Large reverse voltage. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 2 | 4 | HALT. Electrical Stress Testing. Thermal Stress Testing. | Clamp board feedback is available to iiDCE. | 1 | 4 | [11 empty] | 5312
SV104-10969 | Low Voltage Detection Voltage Divider | R41,R36 | To set UVLO threshold | Resistor fails-open. | No voltage will be available at power controlling MOSFET gate. On-board 15 V supply will not be available. No output available at HV transformer board. | Clamp board will be unable to get power. Device\s capability to clamp surges via clamp board will not be available. iiDCE will get power via redundant HVT board. Fault current handling via iiDCE and iSCR driver board will be available. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Over voltage. Over Temperature. Over stress due to shock or vibration. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. Vibration testing. | Clamp board feedback is available to iiDCE. | 1 | 2 | [9 empty] | 0 |  | 10969
SV104-10970 |  |  |  | Resistor fails-short. | UVLO limit will decrease. Board will powerup at lower voltage. Board will keep working. | If no other failure is observed on the board, Clamp and iiDCE board will stay powered. Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | Wear-out due to extensive use. Excessive humidity. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. Vibration testing. | None. | 5 | 5 | [11 empty] | 10970
SV104 - 5313 | Input Side Voltage Divider Resistor. | R30,R31,R32,R33,R34,R35 | To step down voltage. | Resistor fails-open. | No voltage will be available at power controlling MOSFET gate. On-board 15 V supply will not be available. No output available at HV transformer board. | Clamp board will be unable to get power. Device\s capability to clamp surges via clamp board will not be available. iiDCE will get power via redundant HVT board. Fault current handling via iiDCE and iSCR driver board will be available. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Over voltage. Over Temperature. Over stress due to shock or vibration. De-gradation of components. Overcurrent. Counterfeit part. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. Vibration testing. | Clamp board feedback is available to iiDCE. | 1 | 2 | [9 empty] | 0 |  | 5313
SV104 - 5314 |  |  |  | Any one resistor fails-short. | No immediate effect on board. Board will keep working normally. | If no other failure is observed on the board, Clamp and iiDCE board will stay powered. Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | Wear-out due to extensive use. Excessive humidity. Counterfeit part. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. Vibration testing. | Clamp board feedback is available to iiDCE. | 1 | 1 | [11 empty] | 5314
SV104-12387 |  |  |  | More than one resistors fails-short. | Soft starting current is increased significantly consequently MOSFET power dissipation will increase that could bring failure. No output available at HV transformer board. | Clamp board will be unable to get power. Device\s capability to clamp surges via clamp board will not be available. iiDCE will get power via redundant HVT board. Fault current handling via iiDCE and iSCR driver board will be available. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Wear-out due to extensive use. Excessive humidity. Counterfeit part. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements.. Conformal coating. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. Vibration testing. | Clamp board feedback is available to iiDCE. | 1 | 2 | [11 empty] | 12387
SV104 - 5315 | Input Power Control MOSFET. | Q6 | To turn ON/OFF power flow. | MOSFET fails-open. | Input power path will be broken. No output available at HV transformer board. | Clamp board will be unable to get power. Device\s capability to clamp surges via clamp board will not be available. iiDCE will get power via redundant HVT board. Fault current handling via iiDCE and iSCR driver board will be available. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Overheating Mechanical stress resulting in cracked MOSFET body. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | Clamp board feedback is available to iiDCE. | 1 | 2 | [9 empty] | 0 |  | 5315
SV104 - 5316 |  |  |  | MOSFET fails-short. | Startup circuitry will turn on permanently resulting in overheating and permanently damage to startup resistor. No output available once HV-ISO reboot. | Clamp board will be unable to get power. Device\s capability to clamp surges via clamp board will not be available. iiDCE will get power via redundant HVT board. Fault current handling via iiDCE and iSCR driver board will be available. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Transients Overheating as a result of loose connection with heat sink Overcurrent Counterfeit part Damage during mechanical assembly of board Metallic debris stuck in between terminals | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | Clamp board feedback is available to iiDCE. | 1 | 2 | [11 empty] | 5316
SV104 - 5317 | Over-voltage Protection Zener Diode at MOSFET Gate Side. | D31 | For gate protection of MOSFET. | Diode fails-open. | Over-voltage protection of MOSFET won't be available. No immediate effect on board in normal operations. | If no other failure is observed on the board, Clamp and iiDCE board will stay powered. Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | On-board fault causing higher current flow. Excessive forward current. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 2 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 10 | [9 empty] | 0 |  | 5317
SV104 - 5318 |  |  |  | Diode fails-short. | MOSFET will be turned off completely. Startup circuit will not work. No output available at HV transformer board. | Clamp board will be unable to get power. Device\s capability to clamp surges via clamp board will not be available. iiDCE will get power via redundant HVT board. Fault current handling via iiDCE and iSCR driver board will be available. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Large reverse voltage. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 2 | 4 | HALT. Electrical Stress Testing. Thermal Stress Testing. | Clamp board feedback is available to iiDCE. | 1 | 4 | [11 empty] | 5318
SV104-12388 | Filtration Capacitor | C21 | To suppress noise and remove ripples | Capacitor fails-open. | No immediate effect on board. Board will keep working normally. | If no other failure is observed on the board, Clamp and iiDCE board will stay powered. Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | Mechanical stress. Localized heating for long time will separate end connection of capacitor. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. Vibration Testing. | None. | 5 | 5 | [9 empty] | 0 |  | 12388
SV104-12389 |  |  |  | Capacitor fails-short. | HVDC and 24VAUX will be shorted top ground. Startup circuit will not work. Input Fuse Will be Blown No output available at HV transformer board. | Clamp board will be unable to get power. Device\s capability to clamp surges via clamp board will not be available. iiDCE will get power via redundant HVT board. Fault current handling via iiDCE and iSCR driver board will be available. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Wear-out due to dielectric degradation. High-voltage transients. De-gradation of components. Water ingress during humidity condition as it is film capacitor. Overvoltage | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. Environmental Testing. | Clamp board feedback is available to iiDCE. | 1 | 2 | [11 empty] | 12389
SV104-10971 | MOSFET resistance for Miller Capacitance | R37 | To discharge miller capacitance of MOSFET | Resistor fails-open | Abnormal Behavior of MOSFET Might turn ON/OFF abnormally. Once Board Reboots no output will be available No output available at HV transformer board | Clamp board will be unable to get power. Device\s capability to clamp surges via clamp board will not be available. iiDCE will get power via redundant HVT board. Fault current handling via iiDCE and iSCR driver board will be available. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Over voltage. Over Temperature. Over stress due to shock or vibration. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. Vibration testing. | Clamp board feedback is available to iiDCE. | 1 | 2 | [11 empty] | 10971
SV104-10972 |  |  |  | Resistor fails-short | Gate and Source of Q6 will have no voltage difference so MOSFET cannot operate No output available at HV transformer board | Clamp board will be unable to get power. Device\s capability to clamp surges via clamp board will not be available. iiDCE will get power via redundant HVT board. Fault current handling via iiDCE and iSCR driver board will be available. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Wear-out due to extensive use. Excessive humidity. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. Vibration testing. | Clamp board feedback is available to iiDCE. | 1 | 2 | [11 empty] | 10972
SV104 - 6780 | D21-Free wheeling diode | D21 | To protect BJT during reverse voltage condition | Diode fails-open. | No protection for BJT will be available. Reverse voltage development across BJT will damage it. No output available. | Clamp board will be unable to get power. Device\s capability to clamp surges via clamp board will not be available. iiDCE will get power via redundant HVT board. Fault current handling via iiDCE and iSCR driver board will be available. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | On-board fault causing higher current flow. Excessive forward current. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | Clamp board feedback is available to iiDCE. | 1 | 2 | [11 empty] | 6780
SV104 - 6781 |  |  |  | Diode fails-short. | Input will appear as it is on output which will damage PWM controller and gate driver ICs permanently. No output available. | Clamp board will be unable to get power. Device\s capability to clamp surges via clamp board will not be available. iiDCE will get power via redundant HVT board. Fault current handling via iiDCE and iSCR driver board will be available. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Large reverse voltage. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | Clamp board feedback is available to iiDCE. | 1 | 2 | [11 empty] | 6781
SV104 - 6782 | D22-To prevent reverse power flow | D22 | To prevent reverse power flow from auxiliary to startup circuitry | Diode fails-open. | Input power path will be broken. No output available at HV transformer board. | Clamp board will be unable to get power. Device\s capability to clamp surges via clamp board will not be available. iiDCE will get power via redundant HVT board. Fault current handling via iiDCE and iSCR driver board will be available. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | On-board fault causing higher current flow. Excessive forward current. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | Clamp board feedback is available to iiDCE. | 1 | 2 | [11 empty] | 6782
SV104 - 6783 |  |  |  | Diode fails-short. | If the board is OFF than it can not turn ON. If board is ON than reverse power will start to flow. D31 will be forward biased and as gate of Q6 is grounded than 24VAUX will also be grounded. No output available at HV transformer board. | Clamp board will be unable to get power. Device\s capability to clamp surges via clamp board will not be available. iiDCE will get power via redundant HVT board. Fault current handling via iiDCE and iSCR driver board will be available. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Large reverse voltage. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | Clamp board feedback is available to iiDCE. | 1 | 2 | [11 empty] | 6783
SV104 - 6784 | D27-Zener diode | D27 | To set reference voltage for BJT to regulate | Diode fails-open. | Voltage at input will appear as it is on base damaging it permanently. No output available at HV transformer board. | Clamp board will be unable to get power. Device\s capability to clamp surges via clamp board will not be available. iiDCE will get power via redundant HVT board. Fault current handling via iiDCE and iSCR driver board will be available. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Electrical, Mechanical or environmental overstress. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 2 | 4 | HALT. Electrical Stress Testing. Thermal Stress Testing. | Clamp board feedback is available to iiDCE. | 1 | 4 | [11 empty] | 6784
SV104 - 6785 |  |  |  | Diode fails-short. | BJT will not turn on. No output available at HV transformer board. | Clamp board will be unable to get power. Device\s capability to clamp surges via clamp board will not be available. iiDCE will get power via redundant HVT board. Fault current handling via iiDCE and iSCR driver board will be available. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Excessive Temperature. Overcurrent. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 2 | 4 | HALT. Electrical Stress Testing. Thermal Stress Testing. | Clamp board feedback is available to iiDCE. | 1 | 4 | [11 empty] | 6785
SV104 - 5319 | Input Power Control BJT. | Q8 | To provide regulated voltage for startup. | BJT fails-open. | Input power path will be broken. No output available at HV transformer board. | Clamp board will be unable to get power. Device\s capability to clamp surges via clamp board will not be available. iiDCE will get power via redundant HVT board. Fault current handling via iiDCE and iSCR driver board will be available. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Melted connections due to overheating. Manufacturing defect. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | Clamp board feedback is available to iiDCE. | 1 | 2 | [11 empty] | 5319
SV104 - 5320 |  |  |  | BJT fails-short. | Higher voltage at startup will damage the PWM controller and gate drivers of board. Input power path will be broken. No output available at HV transformer board. | Clamp board will be unable to get power. Device\s capability to clamp surges via clamp board will not be available. iiDCE will get power via redundant HVT board. Fault current handling via iiDCE and iSCR driver board will be available. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Over voltage. Leaky junctions. Wear-out due to high power dissipation. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | Clamp board feedback is available to iiDCE. | 1 | 2 | [11 empty] | 5320
SV104 - 5321 | Biasing Resistor for BJT. | R40 | To set biasing threshold for power flow controlling BJT. | Resistor fails-open. | BJT will be permanently turned OFF. Input power path will be broken. No output available at HV transformer board. | Clamp board will be unable to get power. Device\s capability to clamp surges via clamp board will not be available. iiDCE will get power via redundant HVT board. Fault current handling via iiDCE and iSCR driver board will be available. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Over voltage. Over Temperature. Over stress due to shock or vibration. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | Clamp board feedback is available to iiDCE. | 1 | 2 | [9 empty] | 0 |  | 5321
SV104 - 5322 |  |  |  | Resistor fails-short. | 24 V will be replicated at the emitter for the shorted duration, on-board ICs may get burn due to this over-voltage. BJT will eventually fail-open due to over-current. Input power path will be broken. No output available at HV transformer board. | Clamp board will be unable to get power. Device\s capability to clamp surges via clamp board will not be available. iiDCE will get power via redundant HVT board. Fault current handling via iiDCE and iSCR driver board will be available. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Wear-out due to extensive use. Excessive humidity. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | Clamp board feedback is available to iiDCE. | 1 | 2 | [11 empty] | 5322
SV104 - 5323 | Freewheeling Diode. | z | To provide reverser current flow path. | Diode fails-open. | No path will be available for reverse current to flow. Potential difference creation across BJT can damage the BJT. Input power path will be broken. No output available at HV transformer board. | Clamp board will be unable to get power. Device\s capability to clamp surges via clamp board will not be available. iiDCE will get power via redundant HVT board. Fault current handling via iiDCE and iSCR driver board will be available. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Excessive forward current flow. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | Clamp board feedback is available to iiDCE. | 1 | 2 | [11 empty] | 5323
SV104 - 5324 |  |  |  | Diode fails-short. | An emitter to collector short on BJT will cause the BJT to over-heat and may fail-open. Input power path will be broken. No output available at HV transformer board. | Clamp board will be unable to get power. Device\s capability to clamp surges via clamp board will not be available. iiDCE will get power via redundant HVT board. Fault current handling via iiDCE and iSCR driver board will be available. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Large reverse voltage. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | Clamp board feedback is available to iiDCE. | 1 | 2 | [11 empty] | 5324
SV104 - 5325 | 15 V Rail Output Side Capacitors. | C22,C19,C20 | To stable output voltage and to suppress ripples. | Capacitor fails-open. | No immediate effect on board.. | If no other failure is observed on the board, Clamp and iiDCE board will stay powered. Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | Mechanical stress. Localized heating for long time will separate end connection of capacitor. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [11 empty] | 5325
SV104 - 5326 |  |  |  | Capacitor fails-short. | 15 V power supply will be shorted to ground. On-board electronics will not be powered up. No output available at HV transformer board. | Clamp board will be unable to get power. Device\s capability to clamp surges via clamp board will not be available. iiDCE will get power via redundant HVT board. Fault current handling via iiDCE and iSCR driver board will be available. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Wear-out due to dielectric degradation. High-voltage transients. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | Clamp board feedback is available to iiDCE. | 1 | 2 | [9 empty] | 0 |  | 5326
SV104 - 5327 | 24 V Feedback Signal Side Resistor. | R38 | To provide 24 V sensing feedback path. | Resistor fails-open. | 15 V regulator will keep on working from input side and will not turn off. Which will heat up the resistor on MOSFET Q6 drain and will burn out eventually. No output available at HV transformer board. | Clamp board will be unable to get power. Device\s capability to clamp surges via clamp board will not be available. iiDCE will get power via redundant HVT board. Fault current handling via iiDCE and iSCR driver board will be available. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Over voltage. Over Temperature. Over stress due to shock or vibration. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | Clamp board feedback is available to iiDCE. | 1 | 2 | [9 empty] | 0 |  | 5327
SV104 - 5328 |  |  |  | Resistor fails-short. | Over-current will cause the resistor to eventually fail-open. 15 V regulator will keep on working from input side and will not turn off. Which will heat up the resistor on MOSFET Q6 drain and will burn out eventually. No output available at HV transformer board. | Clamp board will be unable to get power. Device\s capability to clamp surges via clamp board will not be available. iiDCE will get power via redundant HVT board. Fault current handling via iiDCE and iSCR driver board will be available. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Wear-out due to extensive use. Excessive humidity. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | Clamp board feedback is available to iiDCE. | 1 | 2 | [9 empty] | 0 |  | 5328
SV104 - 5329 | 24 V Feedback Signal Side 9 V Zener Diode. | D23 | To maintain a constant 9 V drop. To turn off the startup circuitry once full bridge auxiliary supply exceeds 9.1 V. | Diode fails-open. | 15 V regulator will keep on working from input side and will not turn off. Which will heat up the resistor on MOSFET Q6 drain and will burn out eventually. No output available at HV transformer board. | Clamp board will be unable to get power. Device\s capability to clamp surges via clamp board will not be available. iiDCE will get power via redundant HVT board. Fault current handling via iiDCE and iSCR driver board will be available. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Excessive Temperature. Overcurrent. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 2 | 4 | HALT. Electrical Stress Testing. Thermal Stress Testing. | Clamp board feedback is available to iiDCE. | 1 | 4 | [9 empty] | 0 |  | 5329
SV104 - 5330 |  |  |  | Diode fails-short. | Startup circuitry will be turned off before full bridge secondary is activated completely. As a result startup circuitry will keep activating and then turn off due to aux voltage. This will eventually damage the startup circuitry of board. No output available at HV transformer board. | Clamp board will be unable to get power. Device\s capability to clamp surges via clamp board will not be available. iiDCE will get power via redundant HVT board. Fault current handling via iiDCE and iSCR driver board will be available. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Over voltage. Over Temperature. Over stress due to shock or vibration. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 2 | 4 | HALT. Electrical Stress Testing. Thermal Stress Testing. | Clamp board feedback is available to iiDCE. | 1 | 4 | [11 empty] | 5330
SV104 - 6786 | 24 V Feedback Signal Side - R39 | R39 | Voltage divider resistor-Low side | Resistor fails-open | 15 V regulator will keep on working from input side and will not turn off. Which will heat up the resistor on MOSFET Q6 drain and will burn out eventually. No output available at HV transformer board. | Clamp board will be unable to get power. Device\s capability to clamp surges via clamp board will not be available. iiDCE will get power via redundant HVT board. Fault current handling via iiDCE and iSCR driver board will be available. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Over voltage. Over Temperature. Over stress due to shock or vibration. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | Clamp board feedback is available to iiDCE. | 1 | 2 | [9 empty] | 0 |  | 6786
SV104 - 6787 |  |  |  | Resistor fails-short | 15 V regulator will keep on working from input side and will not turn off. Which will heat up the resistor on MOSFET Q6 drain and will burn out eventually. No output available at HV transformer board. | Clamp board will be unable to get power. Device\s capability to clamp surges via clamp board will not be available. iiDCE will get power via redundant HVT board. Fault current handling via iiDCE and iSCR driver board will be available. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Wear-out due to extensive use. Excessive humidity. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | Clamp board feedback is available to iiDCE. | 1 | 2 | [11 empty] | 6787
SV104 - 6788 | 24 V Feedback Signal Side - D23 | D23 | To maintain a constant 9 V drop. To turn off the startup circuitry once full bridge auxiliary supply exceeds 9.1 V. | Diode fails-open | 15 V regulator will keep on working from input side and will not turn off. Which will heat up the resistor on MOSFET Q6 drain and will burn out eventually. No output available at HV transformer board. | Clamp board will be unable to get power. Device\s capability to clamp surges via clamp board will not be available. iiDCE will get power via redundant HVT board. Fault current handling via iiDCE and iSCR driver board will be available. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Excessive forward current flow. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | Clamp board feedback is available to iiDCE. | 1 | 2 | [9 empty] | 0 |  | 6788
SV104 - 6789 |  |  |  | Diode fails-short | No immediate effect on board. | If no other failure is observed on the board, Clamp and iiDCE board will stay powered. Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | Large reverse voltage. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [11 empty] | 6789
SV104 - 6790 | 24 V Feedback Signal Side - D24 | D24 | To prevent reverse power flow from startup circuitry | Diode fails-open | As soon as auxiliary will develop board will be disabled and power-up again and this cycle will keep repeating which will damage the startup circuitry permanently. No output available at HV transformer board. | Clamp board will be unable to get power. Device\s capability to clamp surges via clamp board will not be available. iiDCE will get power via redundant HVT board. Fault current handling via iiDCE and iSCR driver board will be available. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Excessive forward current flow. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | Clamp board feedback is available to iiDCE. | 1 | 2 | [9 empty] | 0 |  | 6790
SV104 - 6791 |  |  |  | Diode fails-short | Startup circuitry will disable itself before powering up the board. It will happen repeatedly eventually damaging the startup circuitry. No output available at HV transformer board. | Clamp board will be unable to get power. Device\s capability to clamp surges via clamp board will not be available. iiDCE will get power via redundant HVT board. Fault current handling via iiDCE and iSCR driver board will be available. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Large reverse voltage. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | Clamp board feedback is available to iiDCE. | 1 | 2 | [11 empty] | 6791
SV104 - 6792 | 24 V Feedback Signal Side - D26 | D26 | Overvoltage protection for MOSFET | Diode fails-open | No immediate effect on board. | If no other failure is observed on the board, Clamp and iiDCE board will stay powered. Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | Excessive forward current flow. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 2 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 10 | [11 empty] | 6792
SV104 - 6793 |  |  |  | Diode fails-short | 15 V regulator will keep on working from input side and will not turn off. Which will heat up the resistor on MOSFET Q6 drain and will burn out eventually. No output available at HV transformer board. | Clamp board will be unable to get power. Device\s capability to clamp surges via clamp board will not be available. iiDCE will get power via redundant HVT board. Fault current handling via iiDCE and iSCR driver board will be available. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Large reverse voltage. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 2 | 4 | HALT. Electrical Stress Testing. Thermal Stress Testing. | Clamp board feedback is available to iiDCE. | 1 | 4 | [11 empty] | 6793
SV104 - 5331 | 24 V Feedback Signal Side MOSFET. | Q7 | To turn OFF power flow controlling MOSFET when auxiliary voltage develops. | MOSFET fails-open. | 15 V regulator will keep on working from input side and will not turn off. Which will heat up the resistor on MOSFET Q6 drain and will burn out eventually. No output available at HV transformer board. | Clamp board will be unable to get power. Device\s capability to clamp surges via clamp board will not be available. iiDCE will get power via redundant HVT board. Fault current handling via iiDCE and iSCR driver board will be available. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Overheating Mechanical stress resulting in cracked MOSFET body. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | Clamp board feedback is available to iiDCE. | 1 | 2 | [9 empty] | 0 |  | 5331
SV104 - 5332 |  |  |  | MOSFET fails-short. | Startup circuitry will remain off permanently as Q6 remains off permanently. 15 V regulator will keep on working from input side and will not turn off. Which will heat up the resistor on MOSFET Q6 drain and will burn out eventually. No output available at HV transformer board. | Clamp board will be unable to get power. Device\s capability to clamp surges via clamp board will not be available. iiDCE will get power via redundant HVT board. Fault current handling via iiDCE and iSCR driver board will be available. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Transients Overheating as a result of loose connection with heat sink Overcurrent Counterfeit part Damage during mechanical assembly of board Metallic debris stuck in between terminals | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | Clamp board feedback is available to iiDCE. | 1 | 2 | [11 empty] | 5332
SV104 - 5333 | 24 V Feedback Signal Side MOSFET.- Zener at Gate | D25 | To protect MOSFET (Q6) gate from over-voltage. | Diode fails-open. | Over-voltage protection of MOSFET won't be available. No immediate effect on board in normal operations. | If no other failure is observed on the board, Clamp and iiDCE board will stay powered. Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | Excessive forward current flow. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 2 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 10 | [9 empty] | 0 |  | 5333
SV104 - 5334 |  |  |  | Diode fails-short. | Board will not power up as startup circuit will remain off. Q6 will remain permanently off. No output available at HV transformer board. | Clamp board will be unable to get power. Device\s capability to clamp surges via clamp board will not be available. iiDCE will get power via redundant HVT board. Fault current handling via iiDCE and iSCR driver board will be available. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Large reverse voltage. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 2 | 4 | HALT. Electrical Stress Testing. Thermal Stress Testing. | Clamp board feedback is available to iiDCE. | 1 | 4 | [11 empty] | 5334
| PWM Controller | [26 empty] | 0
SV104 - 5335 | PWM Controller IC. | U1 | To provide alternate PWM pulses for full bridge gate driver. | IC output is permanently low. | No PWM will be available for half bridge driver ICs, No output available at HV transformer board. | Clamp board will be unable to get power. Device\s capability to clamp surges via clamp board will not be available. iiDCE will get power via redundant HVT board. Fault current handling via iiDCE and iSCR driver board will be available. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Electrical Overstress. ESD. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | Clamp board feedback is available to iiDCE. | 1 | 2 | [11 empty] | 5335
SV104 - 5336 |  |  |  | One of output is permanently high. | Output of Full Bridge circuit will be 12 V at no load. HV transformer board will have no output as soon as load is applied. | Clamp board will be unable to get power. Device\s capability to clamp surges via clamp board will not be available. iiDCE will get power via redundant HVT board. Fault current handling via iiDCE and iSCR driver board will be available. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Electrical Overstress. ESD. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | Clamp board feedback is available to iiDCE. | 1 | 2 | [9 empty] | 0 |  | 5336
SV104 - 5337 |  |  |  | PWM is having different duty cycle than desired. | Output of Full Bridge circuit will have different duty cycle. HV transformer board will have more or less than 24 V output. | If no other failure is observed on the board, Clamp and iiDCE board will stay powered. Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | Internal IC damage. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 2 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 10 | [11 empty] | 5337
SV104 - 5338 | Line Under-Voltage Lockout Voltage Divider High Side Resistor. | R1 | To turn OFF gate driver PWM in case of under-voltage. | Resistor fails-open. | PWM controller will remain off permanently. No output available. | Clamp board will be unable to get power. Device\s capability to clamp surges via clamp board will not be available. iiDCE will get power via redundant HVT board. Fault current handling via iiDCE and iSCR driver board will be available. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Over voltage. Over Temperature. Over stress due to shock or vibration. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | Clamp board feedback is available to iiDCE. | 1 | 2 | [9 empty] | 0 |  | 5338
SV104 - 5339 |  |  |  | Resistor fails-short. | UVLO pin will get damaged, No PWM will be available for half bridge driver ICs, No output available at HV transformer board. | Clamp board will be unable to get power. Device\s capability to clamp surges via clamp board will not be available. iiDCE will get power via redundant HVT board. Fault current handling via iiDCE and iSCR driver board will be available. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Wear-out due to extensive use. Excessive humidity. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | Clamp board feedback is available to iiDCE. | 1 | 2 | [11 empty] | 5339
SV104 - 5340 | Line Under-Voltage Lockout Voltage Divider Low Side Resistor. | R13 | To turn OFF gate driver PWM in case of under-voltage. | Resistor fails-open. | UVLO pin will get damaged, No PWM will be available for half bridge driver ICs, No output available at HV transformer board. Redundant power to iSCR driver board will be cut-off. | Clamp board will be unable to get power. Device\s capability to clamp surges via clamp board will not be available. iiDCE will get power via redundant HVT board. Fault current handling via iiDCE and iSCR driver board will be available. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Over voltage. Over Temperature. Over stress due to shock or vibration. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | Clamp board feedback is available to iiDCE. | 1 | 2 | [11 empty] | 5340
SV104 - 5341 |  |  |  | Resistor fails-short. | PWM controller will remain off permanently. No output available. | Clamp board will be unable to get power. Device\s capability to clamp surges via clamp board will not be available. iiDCE will get power via redundant HVT board. Fault current handling via iiDCE and iSCR driver board will be available. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Wear-out due to extensive use. Excessive humidity. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | Clamp board feedback is available to iiDCE. | 1 | 2 | [9 empty] | 0 |  | 5341
SV104 - 5342 | RT2 Biasing Resistor. | R14 | To control oscillator dead time. | Resistor fails-open. | Dead time between alternating PWMs will be altered (maximum). 1 PWM will be permanently high, while other will be permanently low. Output of isolation transformer will not be available. No output available at HV transformer board. | Clamp board will be unable to get power. Device\s capability to clamp surges via clamp board will not be available. iiDCE will get power via redundant HVT board. Fault current handling via iiDCE and iSCR driver board will be available. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Over voltage. Over Temperature. Over stress due to shock or vibration. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | Clamp board feedback is available to iiDCE. | 1 | 2 | [11 empty] | 5342
SV104 - 5343 |  |  |  | Resistor fails-short. | Dead time between alternating PWMs will be altered (maximum). 1 PWM will be permanently high, while other will be permanently low. Output of isolation transformer will not be available. No output available at HV transformer board. | Clamp board will be unable to get power. Device\s capability to clamp surges via clamp board will not be available. iiDCE will get power via redundant HVT board. Fault current handling via iiDCE and iSCR driver board will be available. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Wear-out due to extensive use. Excessive humidity. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | Clamp board feedback is available to iiDCE. | 1 | 2 | [11 empty] | 5343
SV104 - 5344 | RT1 Biasing Resistor. | R15 | To control oscillator maximum ON time. | Resistor fails-open. | Dead time between alternating PWMs will be altered (maximum). 1 PWM will be permanently high, while other will be permanently low. Output of isolation transformer will not be available. No output available at HV transformer board. | Clamp board will be unable to get power. Device\s capability to clamp surges via clamp board will not be available. iiDCE will get power via redundant HVT board. Fault current handling via iiDCE and iSCR driver board will be available. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Over voltage. Over Temperature. Over stress due to shock or vibration. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | Clamp board feedback is available to iiDCE. | 1 | 2 | [11 empty] | 5344
SV104 - 5345 |  |  |  | Resistor fails-short. | Dead time between alternating PWMs will be altered (maximum). 1 PWM will be permanently high, while other will be permanently low. Output of isolation transformer will not be available. No output available at HV transformer board. | Clamp board will be unable to get power. Device\s capability to clamp surges via clamp board will not be available. iiDCE will get power via redundant HVT board. Fault current handling via iiDCE and iSCR driver board will be available. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Wear-out due to extensive use. Excessive humidity. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | Clamp board feedback is available to iiDCE. | 1 | 2 | [11 empty] | 5345
SV104 - 5346 | Restart Timer Resistor. | R16 | To set PWM restart signal biasing. | Resistor fails-open. | Restart timer functionality will be compromised. No immediate effect on board in normal operations. | If no other failure is observed on the board, Clamp and iiDCE board will stay powered. Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | Over voltage. Over Temperature. Over stress due to shock or vibration. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [11 empty] | 5346
SV104 - 5347 |  |  |  | Resistor fails-short. | Restart timer functionality will be compromised. No immediate effect on board in normal operations. | If no other failure is observed on the board, Clamp and iiDCE board will stay powered. Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | Wear-out due to extensive use. Excessive humidity. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [9 empty] | 0 |  | 5347
SV104 - 5348 | Soft-Start Capacitor. | C10 | To provide soft-start biasing value. | Capacitor fails-open. | Soft start functionality will be compromised. No immediate effect on board in normal operations. | If no other failure is observed on the board, Clamp and iiDCE board will stay powered. Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | Mechanical stress. Localized heating for long time will separate end connection of capacitor. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [11 empty] | 5348
SV104 - 5349 |  |  |  | Capacitor fails-short. | PWM controller will turn off permanently. No output available for board. | Clamp board will be unable to get power. Device\s capability to clamp surges via clamp board will not be available. iiDCE will get power via redundant HVT board. Fault current handling via iiDCE and iSCR driver board will be available. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Wear-out due to dielectric degradation. High-voltage transients. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | Clamp board feedback is available to iiDCE. | 1 | 2 | [9 empty] | 0 |  | 5349
SV104 - 5350 | Ramp Control Resistor. | R12 | To provide ramp control of PWM. | Resistor fails-open. | PWM ramp will be affected. Output of Full Bridge circuit will be different than desired. HV transformer board will have more or less than 24 V output. | If no other failure is observed on the board, Clamp and iiDCE board will stay powered. Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | Over voltage. Over Temperature. Over stress due to shock or vibration. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [11 empty] | 5350
SV104 - 5351 |  |  |  | Resistor fails-short. | PWM ramp will be affected. Output of Full Bridge circuit will be different than desired. HV transformer board will have more or less than 24 V output. | If no other failure is observed on the board, Clamp and iiDCE board will stay powered. Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | Wear-out due to extensive use. Excessive humidity. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [11 empty] | 5351
SV104 - 5352 | Current Sense Signal Filtration Capacitor. | C12 | To filter the CS signal. | Capacitor fails-open. | No immediate effect. | If no other failure is observed on the board, Clamp and iiDCE board will stay powered. Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | Mechanical stress. Localized heating for long time will separate end connection of capacitor. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [11 empty] | 5352
SV104 - 5353 |  |  |  | Capacitor fails-short. | Capacitor will fail-open due to over-current. PWM current limiting functionality will be compromised while the capacitor remains shorted. No immediate effect on board in normal operations. | If no other failure is observed on the board, Clamp and iiDCE board will stay powered. Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | Wear-out due to dielectric degradation. High-voltage transients. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [11 empty] | 5353
SV104 - 5354 | Current Sense Capacitor. | C9 | To limit PWM current. | Capacitor fails-open. | PWM current limiting functionality will be compromised. No immediate effect on board in normal operations. | If no other failure is observed on the board, Clamp and iiDCE board will stay powered. Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | Mechanical stress. Localized heating for long time will separate end connection of capacitor. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [11 empty] | 5354
SV104 - 5355 |  |  |  | Capacitor fails-short. | PWM current limiting functionality will be compromised. No immediate effect on board in normal operations. | If no other failure is observed on the board, Clamp and iiDCE board will stay powered. Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | Wear-out due to dielectric degradation. High-voltage transients. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [9 empty] | 0 |  | 5355
SV104-12390 | Decoupling Capacitor | C11 | To Filter Noise | Capacitor fails-open. | No immediate effect on board in normal operations. | If no other failure is observed on the board, Clamp and iiDCE board will stay powered. Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | Mechanical stress. Localized heating for long time will separate end connection of capacitor. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. Vibration Testing. | None. | 5 | 5 | [11 empty] | 12390
SV104-12391 |  |  |  | Capacitor fails-short. | Internal Reference Voltage will be shorted to ground. PWM output will be disabled. Input Fuse Will be Blown No output available at HV transformer board. | Clamp board will be unable to get power. Device\s capability to clamp surges via clamp board will not be available. iiDCE will get power via redundant HVT board. Fault current handling via iiDCE and iSCR driver board will be available. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Wear-out due to dielectric degradation. High-voltage transients. De-gradation of components. Water ingress during humidity condition as it is film capacitor. Overvoltage | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. Environmental Testing. | Clamp board feedback is available to iiDCE. | 1 | 2 | [9 empty] | 0 |  | 12391
SV104-10973 | Input Filtration Capacitance | C1 | To suppress ripples on input voltage. | Capacitor fails-open. | No immediate effect on board due to presence of multiple capacitors at different stages.. | If no other failure is observed on the board, Clamp and iiDCE board will stay powered. Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | Mechanical stress. Localized heating for long time will separate end connection of capacitor. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. Vibration Testing. | None. | 5 | 5 | [11 empty] | 10973
SV104-10974 |  |  |  | Capacitor fails-short. | 15V rail will get shorted to ground thus No output available at HV transformer board . | Clamp board will be unable to get power. Device\s capability to clamp surges via clamp board will not be available. iiDCE will get power via redundant HVT board. Fault current handling via iiDCE and iSCR driver board will be available. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Wear-out due to dielectric degradation. High-voltage transients. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | Clamp board feedback is available to iiDCE. | 1 | 2 | [9 empty] | 0 |  | 10974
SV104-10975 | Current Sense Resistance | R28 | To Sense Overcurrent | Resistor fails-open. | Overcurrent Protection will be compromised during overcurrent condition at primary. No immediate Effect in normal condition. | If no other failure is observed on the board, Clamp and iiDCE board will stay powered. Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | Over voltage. Over Temperature. Over stress due to shock or vibration. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [11 empty] | 10975
SV104-10976 |  |  |  | Resistor fails-short. | IC may trigger False overcurrent and disable output. No output available at HV transformer board | Clamp board will be unable to get power. Device\s capability to clamp surges via clamp board will not be available. iiDCE will get power via redundant HVT board. Fault current handling via iiDCE and iSCR driver board will be available. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Wear-out due to extensive use. Excessive humidity. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | Clamp board feedback is available to iiDCE. | 1 | 2 | [9 empty] | 0 |  | 10976
SV104 - 5356 | Output Driver Resistor. | R4,R5 | To limit gate driver current. | Resistor fails-open. | Gate driver PWM path will be broken. No output available at HV transformer board. | Clamp board will be unable to get power. Device\s capability to clamp surges via clamp board will not be available. iiDCE will get power via redundant HVT board. Fault current handling via iiDCE and iSCR driver board will be available. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Over voltage. Over Temperature. Over stress due to shock or vibration. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | Clamp board feedback is available to iiDCE. | 1 | 2 | [11 empty] | 5356
SV104 - 5357 |  |  |  | Resistor fails-short. | No immediate till the shorted duration. Resistor will fail-open due to over-current. Gate driver PWM path will be broken. No output available at HV transformer board. | Clamp board will be unable to get power. Device\s capability to clamp surges via clamp board will not be available. iiDCE will get power via redundant HVT board. Fault current handling via iiDCE and iSCR driver board will be available. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Wear-out due to extensive use. Excessive humidity. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | Clamp board feedback is available to iiDCE. | 1 | 2 | [11 empty] | 5357
| Full Bridge Circuit | [26 empty] | 0
SV104 - 5358 | Half Bridge Gate Driver IC. | U2, U3 | To provide gate driver signal for half bridge MOSFETs. | Both outputs are permanently low. | One half bridge section will not have output. Output of Full Bridge circuit will be 12 V at no load. HV transformer board will have no output as soon as load is applied. | Clamp board will be unable to get power. Device\s capability to clamp surges via clamp board will not be available. iiDCE will get power via redundant HVT board. Fault current handling via iiDCE and iSCR driver board will be available. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Electrical Overstress (Overvoltage). ESD. Counterfeit part. Stress or impact during assembly. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | Clamp board feedback is available to iiDCE. | 1 | 2 | [11 empty] | 5358
SV104 - 5359 |  |  |  | High side output is permanently low. | Full bridge functionality will be disturbed. No output will be available at HV transformer board as soon as load is applied. | Clamp board will be unable to get power. Device\s capability to clamp surges via clamp board will not be available. iiDCE will get power via redundant HVT board. Fault current handling via iiDCE and iSCR driver board will be available. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Electrical Overstress (Overvoltage). ESD. Counterfeit part. Stress or impact during assembly. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | Clamp board feedback is available to iiDCE. | 1 | 2 | [11 empty] | 5359
SV104 - 5360 |  |  |  | High side output is permanently high. | One MOSFET will be permanently turned ON. During times, when low side MOSFET of same half bridge will turn ON, HV DC line get shorted will ground. Due to high current flow, power MOSFETs may get damaged. Input side fuse will burn out and prevent cascading failures. | Clamp board will be unable to get power. Device\s capability to clamp surges via clamp board will not be available. iiDCE will get power via redundant HVT board. Fault current handling via iiDCE and iSCR driver board will be available. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Electrical Overstress (Overvoltage). ESD. Counterfeit part. Stress or impact during assembly. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | Clamp board feedback is available to iiDCE. | 1 | 2 | [9 empty] | 0 |  | 5360
SV104 - 8902 | Half Bridge Gate Driver IC. | U2, U3 | To provide gate driver signal for half bridge MOSFETs. | Low side output is permanently low. | Full bridge functionality will be disturbed. No output will be available at HV transformer board as soon as load is applied. Redundant power to one of the iiDCE driver board will be cut-off. | Clamp board will be unable to get power. Device\s capability to clamp surges via clamp board will not be available. iiDCE will get power via redundant HVT board. Fault current handling via iiDCE and iSCR driver board will be available. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Electrical Overstress (Overvoltage). ESD. Counterfeit part. Stress or impact during assembly. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | Clamp board feedback is available to iiDCE. | 1 | 2 | [11 empty] | 8902
SV104 - 8903 |  |  |  | Low side output is permanently high. | During times, when high side MOSFET of same half bridge will turn ON, HV DC line get shorted with ground. Due to high current flow, power MOSFETs may get damaged. Input side fuse will burn out and prevent cascading failures. Redundant power to one of the iVSL driver board will be cut-off. | Clamp board will be unable to get power. Device\s capability to clamp surges via clamp board will not be available. iiDCE will get power via redundant HVT board. Fault current handling via iiDCE and iSCR driver board will be available. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Electrical Overstress (Overvoltage). ESD. Counterfeit part. Stress or impact during assembly. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | Clamp board feedback is available to iiDCE. | 1 | 2 | [9 empty] | 0 |  | 8903
SV104 - 8904 |  |  |  | Both outputs are permanently high. | Both MOSFETs will be permanently turned ON. HV DC line will get shorted with ground. Due to high current flow, power MOSFETs may get damaged. Input side fuse will burn out and prevent cascading failures. Redundant power to one of the iVSL driver board will be cut-off. | Clamp board will be unable to get power. Device\s capability to clamp surges via clamp board will not be available. iiDCE will get power via redundant HVT board. Fault current handling via iiDCE and iSCR driver board will be available. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Electrical Overstress (Overvoltage). ESD. Counterfeit part. Stress or impact during assembly. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | Clamp board feedback is available to iiDCE. | 1 | 2 | [11 empty] | 8904
SV104 - 5361 | Half Bridge Gate Driver IC - Filter Capacitor. | C4,C5 | To provide high side gate driver floating supply. | Capacitor fails-open. | Output of gate driver IC will be affected. No output available at HV transformer board. | Clamp board will be unable to get power. Device\s capability to clamp surges via clamp board will not be available. iiDCE will get power via redundant HVT board. Fault current handling via iiDCE and iSCR driver board will be available. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Mechanical stress. Localized heating for long time will separate end connection of capacitor. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | Clamp board feedback is available to iiDCE. | 1 | 2 | [9 empty] | 0 |  | 5361
SV104 - 5362 |  |  |  | Capacitor fail short. | Output of gate driver IC will be affected. No output available at HV transformer board. | Clamp board will be unable to get power. Device\s capability to clamp surges via clamp board will not be available. iiDCE will get power via redundant HVT board. Fault current handling via iiDCE and iSCR driver board will be available. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | On-board fault causing higher current flow. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | Clamp board feedback is available to iiDCE. | 1 | 2 | [11 empty] | 5362
SV104 - 5363 | Gate Driver Output Circuit - Resistor. | R7,R24,R6,R23 | To provide path between gate driver IC and gate. | Resistor fails-open. | Output path of gate driver IC will be broken for one MOSFET. Distorted square wave will be available at full bridge circuit output. HV transformer board will have lesser output than desired. | If no other failure is observed on the board, Clamp and iiDCE board will stay powered. Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | Over voltage. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [9 empty] | 0 |  | 5363
SV104 - 5364 |  |  |  | Resistor fails-short. | Over-current will cause the resistor to eventually fail-open. Output path of gate driver IC will be broken for one MOSFET. Distorted square wave will be available at full bridge circuit output. HV transformer board will have lesser output than desired. | If no other failure is observed on the board, Clamp and iiDCE board will stay powered. Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | Over voltage. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [11 empty] | 5364
SV104 - 5365 | Gate Driver Output Circuit - General Purpose Diode. | D1,D2,D3,D4 | To turn off the MOSFET quickly through low resistance path at gate. | Diode fails-open. | MOSFET will turn off through larger resistor which will result in increased switching losses. No immediate effect in case of normal operations. | If no other failure is observed on the board, Clamp and iiDCE board will stay powered. Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | Over voltage. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [11 empty] | 5365
SV104 - 5366 |  |  |  | Diode fail-short. | Over-current will cause the diode to eventually fail-open. MOSFET will turn off through larger resistor which will result in increased switching losses. No immediate effect in case of normal operations. | If no other failure is observed on the board, Clamp and iiDCE board will stay powered. Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | Over voltage. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [9 empty] | 0 |  | 5366
SV104-10977 | Gate Driver Output Circuit -Discharge Resistor. | R2,R3,R20,R21 | To provide low resistance path between gate driver IC and gate to discharge gate capacitance. | Resistor fails-open. | Gate Capacitance will discharge slowly through high resistance path thus on/off time will be disturbed Switching losses will increase. No immediate effect ion board. | If no other failure is observed on the board, Clamp and iiDCE board will stay powered. Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | Over voltage. Over Temperature. Over stress due to shock or vibration. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [11 empty] | 10977
SV104-10978 |  |  |  | Resistor fails-short. | Switching losses will increase. No immediate effect on board. | If no other failure is observed on the board, Clamp and iiDCE board will stay powered. Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | Wear-out due to extensive use. Excessive humidity. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [9 empty] | 0 |  | 10978
SV104-10979 | MOSFET resistance for Miller Capacitance | R10,R27,R11,R26 | To discharge capacitance between all terminals of MOSFET | Resistor fails-open | Abnormal Behavior of MOSFET Might turn ON/OFF abnormally and can damage board. No output available at HV transformer board | Clamp board will be unable to get power. Device\s capability to clamp surges via clamp board will not be available. iiDCE will get power via redundant HVT board. Fault current handling via iiDCE and iSCR driver board will be available. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Over voltage. Over Temperature. Over stress due to shock or vibration. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. Vibration testing. | Clamp board feedback is available to iiDCE. | 1 | 2 | [11 empty] | 10979
SV104-10980 |  |  |  | Resistor fails-short | Gate and Source of MOSFET will have no voltage difference so MOSFET cannot operate No output available at HV transformer board | Clamp board will be unable to get power. Device\s capability to clamp surges via clamp board will not be available. iiDCE will get power via redundant HVT board. Fault current handling via iiDCE and iSCR driver board will be available. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Wear-out due to extensive use. Excessive humidity. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. Vibration testing. | Clamp board feedback is available to iiDCE. | 1 | 2 | [11 empty] | 10980
SV104-10981 | Half Bridge Gate Driver IC - High Side Supply Capacitor. | C7,C15,C16,C8 | To provide high side supply and to ensure bootstrapping in order to operate MOSFET. | One Capacitor fails-open. | No immediate effect as the parallel capacitor will be available and will make sure that MOSFET works properly | If no other failure is observed on the board, Clamp and iiDCE board will stay powered. Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | Mechanical stress. Localized heating for long time will separate end connection of capacitor. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [9 empty] | 0 |  | 10981
SV104-10982 |  |  |  | Both Capacitors fails-open. | MOSFET Cannot operate properly No output available at HV transformer board | Clamp board will be unable to get power. Device\s capability to clamp surges via clamp board will not be available. iiDCE will get power via redundant HVT board. Fault current handling via iiDCE and iSCR driver board will be available. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Mechanical stress. Localized heating for long time will separate end connection of capacitor. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | Clamp board feedback is available to iiDCE. | 1 | 2 | [11 empty] | 10982
SV104-10983 |  |  |  | Capacitor fails-short. | MOSFET Cannot operate properly IC may get damaged No output available at HV transformer board | Clamp board will be unable to get power. Device\s capability to clamp surges via clamp board will not be available. iiDCE will get power via redundant HVT board. Fault current handling via iiDCE and iSCR driver board will be available. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Wear-out due to dielectric degradation. High-voltage transients. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | Clamp board feedback is available to iiDCE. | 1 | 2 | [9 empty] | 0 |  | 10983
SV104 - 5367 | Full Bridge Circuit - MOSFET | Q1,Q2,Q3,Q4 | To convert HV DC to HV AC signal. | MOSFET fails-open. | Distorted square wave will be available at full bridge circuit output. HV transformer board will have lesser output than desired. | If no other failure is observed on the board, Clamp and iiDCE board will stay powered. Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | Overheating Mechanical stress resulting in cracked MOSFET body. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [11 empty] | 5367
SV104 - 5368 |  |  |  | MOSFET fails-short. | No voltage will be available at transformer output, for the shorted duration. No output available at HV transformer board. | Clamp board will be unable to get power. Device\s capability to clamp surges via clamp board will not be available. iiDCE will get power via redundant HVT board. Fault current handling via iiDCE and iSCR driver board will be available. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Transients Overheating as a result of loose connection with heat sink Overcurrent Counterfeit part Damage during mechanical assembly of board Metallic debris stuck in between terminals | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | Clamp board feedback is available to iiDCE. | 1 | 2 | [11 empty] | 5368
SV104-10984 | Gate Driver Output Circuit -Pull Down resistance. | R29,R8 | To provide current sense signal to controller | One Resistor fails-open. | Current over limit value will decrease down to half. No immediate affect in normal condition but in case of overloaded condition current limit will be activated early. | If no other failure is observed on the board, Clamp and iiDCE board will stay powered. Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | Over voltage. Over Temperature. Over stress due to shock or vibration. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [11 empty] | 10984
SV104-10985 |  |  |  | Both Resistor fails-open. | Full bridge circuit ground connection will be disconnected No output available at HV transformer board | Clamp board will be unable to get power. Device\s capability to clamp surges via clamp board will not be available. iiDCE will get power via redundant HVT board. Fault current handling via iiDCE and iSCR driver board will be available. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Over voltage. Over Temperature. Over stress due to shock or vibration. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | Clamp board feedback is available to iiDCE. | 1 | 2 | [9 empty] | 0 |  | 10985
SV104-10986 |  |  |  | Resistor fails-short. | No immediate effect in case of normal operations. Overcurrent protection will not be available. | If no other failure is observed on the board, Clamp and iiDCE board will stay powered. Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | Wear-out due to extensive use. Excessive humidity. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [11 empty] | 10986
SV104 - 5369 | HV Isolation Transformer | P113720 | To step down 400 V AC to 24 V AC. | Primary winding fails-open. | No voltage will be available at transformer output. No output available at HV transformer board. | Clamp board will be unable to get power. Device\s capability to clamp surges via clamp board will not be available. iiDCE will get power via redundant HVT board. Fault current handling via iiDCE and iSCR driver board will be available. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | High operating temperature. Overloading. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | Clamp board feedback is available to iiDCE. | 1 | 2 | [11 empty] | 5369
SV104 - 5370 |  |  |  | Secondary winding fails-open. | No output available at HV transformer board. | Clamp board will be unable to get power. Device\s capability to clamp surges via clamp board will not be available. iiDCE will get power via redundant HVT board. Fault current handling via iiDCE and iSCR driver board will be available. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | High operating temperature. Overloading. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | Clamp board feedback is available to iiDCE. | 1 | 2 | [11 empty] | 5370
SV104 - 5371 |  |  |  | Core degradation. | Output voltage will be less than desired value. | If no other failure is observed on the board, Clamp and iiDCE board will stay powered. Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | Over voltage. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [11 empty] | 5371
SV104 - 5372 |  |  |  | Winding insulation melting. | Turn ratio of transformer will be affected. Output voltage will be less than desired value. | If no other failure is observed on the board, Clamp and iiDCE board will stay powered. Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | Over voltage. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [9 empty] | 0 |  | 5372
SV104 - 6794 |  |  |  | Isolation Failure. | If failure is such that board cannot provide any level of isolation then it will damage clamp and iiDCE board. iiDCE and clamp board will not be powered up. | In case of complete isolation failure controls and communication will not be available. If the device was in injection mode it will switch to monitoring mode. | Affected device and associated group will not be able to enter injection mode. System will keep working normally with reduced injection capability. | 5 | Temperature cycling. Manufacturing Deficiency. Vibration. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 5 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 25 | [9 empty] | 0 |  | 6794
SV104 - 6795 |  |  |  | Auxiliary winding failure(Open) | No auxiliary voltage will be available. Startup circuit will not shutdown eventually burning out. No output will be available for HV-ISO board | Clamp board will be unable to get power. Device\s capability to clamp surges via clamp board will not be available. iiDCE will get power via redundant HVT board. Fault current handling via iiDCE and iSCR driver board will be available. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Over voltage. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | Clamp board feedback is available to iiDCE. | 1 | 2 | [9 empty] | 0 |  | 6795
SV104 - 6796 |  |  |  | Post insulator fails | Insulator failure will not have impact during normal condition as it is to prevent early partial discharge during humid condition. This will not impact bypass side board in any condition but will be critical for MVAR side board in condensed humidity condition. If failure is such that board cannot provide any level of isolation then it will damage iiDCE and iClamp board. | Controls and communication will not be available. If the device was in injection mode it will switch to monitoring mode. | Affected device and associated group will not be able to enter injection mode. System will keep working normally with reduced injection capability. | 5 | Corrosion. Manufacturing Deficiency. Vibration. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 5 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 25 | [11 empty] | 6796
SV104 - 6797 |  |  |  | Potting crack or physical damage | Partial discharge will start resulting in degradation of isolation barrier with the time. No immediate effect as isolation of even 400 Vrms will be enough for normal operation of iVSL driver board. | If no other failure is observed on the board, Clamp and iiDCE board will stay powered. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Manufacturing Deficiency. Vibration. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 10 | [9 empty] | 0 |  | 6797
SV104 - 5373 | HV Isolation Transformer - output Side Full Rectifier - Diode | D5,D6,D8 | To convert 24 V AC to 24 V DC. | Diode fails-open. | Output cut to half if half side is working. | Clamp board will be unable to get power. Device\s capability to clamp surges via clamp board will not be available. iiDCE will get power via redundant HVT board. Fault current handling via iiDCE and iSCR driver board will be available. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Excessive forward current flow. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | Clamp board feedback is available to iiDCE. | 1 | 2 | [11 empty] | 5373
SV104 - 5374 |  |  |  | Diode fails-short. | Secondary winding will get shorted if any diode fails-short. As a result of shortage, excessive amount of current will flow damaging two diodes permanently. Diodes will eventually get open and no output will be available | Clamp board will be unable to get power. Device\s capability to clamp surges via clamp board will not be available. iiDCE will get power via redundant HVT board. Fault current handling via iiDCE and iSCR driver board will be available. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Large reverse voltage. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | Clamp board feedback is available to iiDCE. | 1 | 2 | [11 empty] | 5374
SV104 - 5229 | Output Side Capacitor. | C13,C14 | To suppress output side ripples and to provide filtration. | Capacitor fails-open. | Output voltage may have ripples. No immediate effect on HV transformer board output. | If no other failure is observed on the board, Clamp and iiDCE board will stay powered. Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | Mechanical stress. Localized heating for long time will separate end connection of capacitor. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [11 empty] | 5229
SV104 - 5230 |  |  |  | Capacitor fails-short. | No voltage available at the output for the shorted duration. | Clamp board will be unable to get power. Device\s capability to clamp surges via clamp board will not be available. iiDCE will get power via redundant HVT board. Fault current handling via iiDCE and iSCR driver board will be available. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Wear-out due to dielectric degradation. High-voltage transients. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | Clamp board feedback is available to iiDCE. | 1 | 2 | [9 empty] | 0 |  | 5230
SV104 - 5375 | HV Isolation Transformer - Feedback Side Full Rectifier - Diode | D15,D16,D19,D20 | To convert 24 V AC to 24 V DC for feedback. | Diode fails-open. | Output cut to half if half side is working. | Clamp board will be unable to get power. Device\s capability to clamp surges via clamp board will not be available. iiDCE will get power via redundant HVT board. Fault current handling via iiDCE and iSCR driver board will be available. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Excessive forward current flow. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | Clamp board feedback is available to iiDCE. | 1 | 2 | [9 empty] | 0 |  | 5375
SV104 - 5376 |  |  |  | Diode fails-short. | Secondary winding will get shorted if any diode fails-short. As a result of shortage, excessive amount of current will flow damaging two diodes permanently. Diodes will eventually get open and no output will be available | Clamp board will be unable to get power. Device\s capability to clamp surges via clamp board will not be available. iiDCE will get power via redundant HVT board. Fault current handling via iiDCE and iSCR driver board will be available. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Large reverse voltage. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | Clamp board feedback is available to iiDCE. | 1 | 2 | [11 empty] | 5376
SV104 - 5377 | Output Side Capacitor. | C17,C18 | To suppress output side ripples and to provide filtration. | Capacitor fails-open. | Output voltage may have ripples. No immediate effect on HV transformer board output. | If no other failure is observed on the board, Clamp and iiDCE board will stay powered. Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | Mechanical stress. Localized heating for long time will separate end connection of capacitor. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [11 empty] | 5377
SV104 - 5378 |  |  |  | Capacitor fails-short. | No voltage available at the output for the shorted duration. | Clamp board will be unable to get power. Device\s capability to clamp surges via clamp board will not be available. iiDCE will get power via redundant HVT board. Fault current handling via iiDCE and iSCR driver board will be available. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Wear-out due to dielectric degradation. High-voltage transients. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | Clamp board feedback is available to iiDCE. | 1 | 2 | [11 empty] | 5378
SV104-10987 | Current Limiting resistance for LED (D9) | R44 | To limit current through the LED (D9) | Resistor fails-open | LED indication functionality will be compromised No immediate effect on HV transformer board output. | If no other failure is observed on the board, Clamp and iiDCE board will stay powered. Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | Over voltage. Over Temperature. Over stress due to shock or vibration. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. Vibration testing. | None. | 5 | 5 | [11 empty] | 10987
SV104-10988 |  |  |  | Resistor fails-short | LED indication functionality will be compromised No immediate effect on HV transformer board output. | If no other failure is observed on the board, Clamp and iiDCE board will stay powered. Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | Wear-out due to extensive use. Excessive humidity. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. Vibration testing. | None. | 5 | 5 | [11 empty] | 10988
SV104-10989 | LED for status indication of voltage produced | D9 | Visual indication for board output status | Diode fails-open | LED indication functionality will be compromised No immediate effect on HV transformer board output. | If no other failure is observed on the board, Clamp and iiDCE board will stay powered. Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | Over voltage. Over Temperature. Over stress due to shock or vibration. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. Vibration testing. | None. | 5 | 5 | [11 empty] | 10989
SV104-10990 |  |  |  | Diode fails-short | LED indication functionality will be compromised No immediate effect on HV transformer board output. | If no other failure is observed on the board, Clamp and iiDCE board will stay powered. Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | Wear-out due to extensive use. Excessive humidity. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. Vibration testing. | None. | 5 | 5 | [11 empty] | 10990
SV104-10991 | Load at output | R42,R43 | To keep open load voltage within a range | Resistor fails-open | No immediate effect on board. | If no other failure is observed on the board, Clamp and iiDCE board will stay powered. Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | Over voltage. Over Temperature. Over stress due to shock or vibration. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. Vibration testing. | None. | 5 | 5 | [11 empty] | 10991
SV104-10992 |  |  |  | Resistor fails-short | 24V supply will be shorted out to ground. Resistance will eventually fail open due to over current. No output available at HV transformer board | Clamp board will be unable to get power. Device\s capability to clamp surges via clamp board will not be available. iiDCE will get power via redundant HVT board. Fault current handling via iiDCE and iSCR driver board will be available. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Wear-out due to extensive use. Excessive humidity. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. Vibration testing. | Clamp board feedback is available to iiDCE. | 1 | 2 | [11 empty] | 10992
SV104 - 5379 | Heat Sink | HS1,HS2,HS3,HS4,HS5,HS6,HS7,HS8. | To provide cooling functionality for power components. | Loose connection between heat sink and power component. | Affected component will face high temperature rise during nominal current operations. Power component may get damaged causing HV transformer board output voltage to drop. | Clamp board will be unable to get power. Device\s capability to clamp surges via clamp board will not be available. iiDCE will get power via redundant HVT board. Fault current handling via iiDCE and iSCR driver board will be available. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | External overstress. Mis-handling. Excessive temperature causing joint melts. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 2 | 4 | HALT. Electrical Stress Testing. Thermal Stress Testing. | Clamp board feedback is available to iiDCE. | 1 | 4 | [11 empty] | 5379
SV104-11419 | Secondary Winding Connector | J2 | Secondary of transformer | Connector Disconnected by external Force. | Secondary winding will be opened. No output available at HV transformer board. | Clamp board will be unable to get power. Device\s capability to clamp surges via clamp board will not be available. iiDCE will get power via redundant HVT board. Fault current handling via iiDCE and iSCR driver board will be available. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Open Connections due to vibrations, mis-handling or mechanical stress. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. Vibration Testing. | Clamp board feedback is available to iiDCE. | 1 | 2 | [9 empty] | 0 |  | 11419
SV104-11420 |  |  |  | Connector Burned out | Due to sparking connector will heat up and eventually burnout No output available at HV transformer board. | Clamp board will be unable to get power. Device\s capability to clamp surges via clamp board will not be available. iiDCE will get power via redundant HVT board. Fault current handling via iiDCE and iSCR driver board will be available. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Connection Loose or Sparking at terminals Open Connections due to vibrations, mis-handling or mechanical stress. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. Vibration Testing. | Clamp board feedback is available to iiDCE. | 1 | 2 | [11 empty] | 11420
SV104-11421 | Low voltage DC output Connector | J4 | Output of HVT board | Connector Disconnected by external Force. | Output path will be broken. No output available at HV transformer board. | Clamp board will be unable to get power. Device\s capability to clamp surges via clamp board will not be available. iiDCE will get power via redundant HVT board. Fault current handling via iiDCE and iSCR driver board will be available. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Open Connections due to vibrations, mis-handling or mechanical stress. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. Vibration Testing. | Clamp board feedback is available to iiDCE. | 1 | 2 | [11 empty] | 11421
SV104-11422 |  |  |  | Connector Burned out | Due to sparking connector will heat up and eventually burnout Output path will be broken. No output available at HV transformer board. | Clamp board will be unable to get power. Device\s capability to clamp surges via clamp board will not be available. iiDCE will get power via redundant HVT board. Fault current handling via iiDCE and iSCR driver board will be available. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Connection Loose or Sparking at terminals Open Connections due to vibrations, mis-handling or mechanical stress. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. Vibration Testing. | Clamp board feedback is available to iiDCE. | 1 | 2 | [11 empty] | 11422
SV104-11423 | Auxiliary winding Connector | J6 | Auxiliary winding of transformer for 24AUX | Connector Disconnected by external Force. | 24AUX path will be broken. Startup circuitry will turn on permanently resulting in overheating and permanently damage to startup resistor. No output available once HV-ISO reboot. | Clamp board will be unable to get power. Device\s capability to clamp surges via clamp board will not be available. iiDCE will get power via redundant HVT board. Fault current handling via iiDCE and iSCR driver board will be available. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Open Connections due to vibrations, mis-handling or mechanical stress. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. Vibration Testing. | Clamp board feedback is available to iiDCE. | 1 | 2 | [9 empty] | 0 |  | 11423
SV104-11424 |  |  |  | Connector Burned out | Due to sparking connector will heat up and eventually burnout 24AUX path will be broken. Startup circuitry will turn on permanently resulting in overheating and permanently damage to startup resistor. No output available once HV-ISO reboot. | Clamp board will be unable to get power. Device\s capability to clamp surges via clamp board will not be available. iiDCE will get power via redundant HVT board. Fault current handling via iiDCE and iSCR driver board will be available. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Connection Loose or Sparking at terminals Open Connections due to vibrations, mis-handling or mechanical stress. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. Vibration Testing. | Clamp board feedback is available to iiDCE. | 1 | 2 | [11 empty] | 11424
SV104-11425 | Primary winding of transformer | J1,J5 | primary winding of transformer | Connector Disconnected by external Force. | No voltage will be available at transformer output. No output available at HV transformer board. | Clamp board will be unable to get power. Device\s capability to clamp surges via clamp board will not be available. iiDCE will get power via redundant HVT board. Fault current handling via iiDCE and iSCR driver board will be available. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Open Connections due to vibrations, mis-handling or mechanical stress. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. Vibration Testing. | Clamp board feedback is available to iiDCE. | 1 | 2 | [11 empty] | 11425
SV104-11426 |  |  |  | Connector Burned out | Due to sparking connector will heat up and eventually burnout No voltage will be available at transformer output. No output available at HV transformer board. | Clamp board will be unable to get power. Device\s capability to clamp surges via clamp board will not be available. iiDCE will get power via redundant HVT board. Fault current handling via iiDCE and iSCR driver board will be available. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Connection Loose or Sparking at terminals Open Connections due to vibrations, mis-handling or mechanical stress. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. Vibration Testing. | Clamp board feedback is available to iiDCE. | 1 | 2 | [11 empty] | 11426
SV104 - 6798 | Connector | J3 | Input connector | Connector shorted | PHT-DC board external capacitor will dump full energy in board. HV-ISO board's input traces will burn out. iiDCE and clamp boards will be damaged permanently. | Controls and communication will not be available. If the device was in injection mode it will switch to monitoring mode. | Affected device and associated group will not be able to enter injection mode. System will keep working normally with reduced injection capability. | 5 | Manufacturing Deficiency. Excessive temperature causing joint melts. Excessive humidity. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 5 | HALT. Electrical Stress Testing. Thermal Stress Testing. | Clamp board feedback is available to iiDCE. | 1 | 5 | [11 empty] | 6798
| HV Transformer Board for 1 MVAr | [26 empty] | 0
| 15 V On-Board Supply | [26 empty] | 0
SV104 - 6799 | Input Side TRIACs. | D13,D12 | Reverse polarity protection. | TRIAC fails-open. | No immediate effect. Parallel TRIAC available for alternate path. | If no other failure is observed on the board, iiSC board will stay powered. Device can operate in both monitoring and injection mode | System will keep working normally. | 1 | On-board fault causing higher current flow. Excessive forward current. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant 24 V supply to iiSC board will be provided via UPSB. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [11 empty] | 6799
SV104 - 6800 |  |  |  | TRIAC fails-short. | Reverse polarity protection will be compromised during shortage. | If no other failure is observed on the board, iiSC board will stay powered. Device can operate in both monitoring and injection mode | System will keep working normally. | 1 | Large reverse voltage. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant 24 V supply to iiSC board will be provided via UPSB. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [11 empty] | 6800
SV104 - 6801 |  |  |  | Both TRIACs fail-short | Reverse polarity protection will be compromised during shortage. Board will keep working normally if input is provided with correct polarity. | If no other failure is observed on the board, iiSC board will stay powered. Device can operate in both monitoring and injection mode | System will keep working normally. | 1 | Large reverse voltage. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant 24 V supply to iiSC board will be provided via UPSB. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [11 empty] | 6801
SV104 - 6802 |  |  |  | Both TRIACs fail-open. | Input path will be broken. No output available at HV transformer board. | iiSC will be unable to get power from HVT board. If previously system was in injection then iiSC will get power from Universal PSB. But if previously system was in monitoring mode and capacitor bank is not charged than iiSC will have no power available. | Affected device and associated group will not be able to enter injection mode. System will keep working normally with reduced injection capability. | 3 | On-board fault causing higher current flow. Excessive forward current. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant 24 V supply to iiSC board will be provided via UPSB. | 1 | 3 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 15 | [9 empty] | 0 |  | 6802
SV104 - 6803 | Input Side Fuse. | F2 | To cut-off supply in case of over-current. | Fuse fails-open. | Input power path will be broken. No output available at HV transformer board. | iiSC will be unable to get power from HVT board. If previously system was in injection then iiSC will get power from Universal PSB. But if previously system was in monitoring mode and capacitor bank is not charged than iiSC will have no power available. | Affected device and associated group will not be able to enter injection mode. System will keep working normally with reduced injection capability. | 3 | On-board fault causing higher current flow. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant 24 V supply to iiSC board will be provided via UPSB. | 1 | 3 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 15 | [11 empty] | 6803
SV104 - 6804 | Input Side Filter Capacitors. | C2,C23 | To suppress ripples on input voltage. | Capacitor fails-open. | Input supply ripples may cause distorted output supply. No immediate effect on board.. | iiSC will be unable to get power from HVT board. If previously system was in injection then iiSC will get power from Universal PSB. But if previously system was in monitoring mode and capacitor bank is not charged than iiSC will have no power available. | System will keep working normally. | 1 | Mechanical stress. Localized heating for long time will separate end connection of capacitor. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant 24 V supply to iiSC board will be provided via UPSB. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [9 empty] | 0 |  | 6804
SV104 - 6805 |  |  |  | Capacitor fails-short. | PHT-DC Capacitor will dump full energy in HV-ISO board leaving it permanently damage (Trace damage). No output available at HV transformer board. | iiSC will be unable to get power from HVT board. If previously system was in injection then iiSC will get power from Universal PSB. But if previously system was in monitoring mode and capacitor bank is not charged than iiSC will have no power available. | Affected device and associated group will not be able to enter injection mode. System will keep working normally with reduced injection capability. | 3 | Wear-out due to dielectric degradation. High-voltage transients. De-gradation of components. Water ingress during humidity condition as it is film capacitor. Overvoltage | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. RTV application on edges to stop water ingress. Redundant 24 V supply to iiSC board will be provided via UPSB. | 1 | 3 | HALT. Electrical Stress Testing. Thermal Stress Testing. Environmental Testing. | None. | 5 | 15 | [11 empty] | 6805
SV104 - 6806 | Low Voltage Detection Zener Diode. (D7, D11, D10) | D7,D10,D11 | To set under-voltage lockout threshold. | Diode fails-open. | No voltage will be available at power controlling MOSFET gate. On-board 15 V supply will not be available. No output available at HV transformer board. Redundant power to one of the iiSC board via HVT will be cut-off. | iiSC will be unable to get power from HVT board. If previously system was in injection then iiSC will get power from Universal PSB. But if previously system was in monitoring mode and capacitor bank is not charged than iiSC will have no power available. | Affected device and associated group will not be able to enter injection mode. System will keep working normally with reduced injection capability. | 3 | On-board fault causing higher current flow. Excessive forward current. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant 24 V supply to iiSC board will be provided via UPSB. | 2 | 6 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 30 | [9 empty] | 0 |  | 6806
SV104 - 6807 |  |  |  | Diode fails-short.. | The threshold for UVLO detection will decrease. Board will turn on before the set threshold of 320 V. Slight effect will be on PHT-DC bus during low line current condition as it will ramp up slowly. Board will keep working. | iiSC will be unable to get power from HVT board. If previously system was in injection then iiSC will get power from Universal PSB. But if previously system was in monitoring mode and capacitor bank is not charged than iiSC will have no power available. | System will keep working normally. | 1 | Large reverse voltage. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant 24 V supply to iiSC board will be provided via UPSB. | 2 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 10 | [11 empty] | 6807
SV104-10993 | Low Voltage Detection Voltage Divider | R41,R36 | To set UVLO threshold | Resistor fails-open. | No voltage will be available at power controlling MOSFET gate. On-board 15 V supply will not be available. No output available at HV transformer board. | iiSC will be unable to get power from HVT board. If previously system was in injection then iiSC will get power from Universal PSB. But if previously system was in monitoring mode and capacitor bank is not charged than iiSC will have no power available. | Affected device and associated group will not be able to enter injection mode. System will keep working normally with reduced injection capability. | 3 | Over voltage. Over Temperature. Over stress due to shock or vibration. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant 24 V supply to iiSC board will be provided via UPSB. | 1 | 3 | HALT. Electrical Stress Testing. Thermal Stress Testing. Vibration testing. | None. | 5 | 15 | [9 empty] | 0 |  | 10993
SV104-10994 |  |  |  | Resistor fails-short. | UVLO limit will decrease. Board will power up at lower voltage. Board will keep working. | iiSC will be unable to get power from HVT board. If previously system was in injection then iiSC will get power from Universal PSB. But if previously system was in monitoring mode and capacitor bank is not charged than iiSC will have no power available. | System will keep working normally. | 1 | Wear-out due to extensive use. Excessive humidity. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant 24 V supply to iiSC board will be provided via UPSB. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. Vibration testing. | None. | 5 | 5 | [11 empty] | 10994
SV104 - 6808 | Input Side Voltage Divider Resistor. | R30,R31,R32,R33,R34,R35 | To step down voltage. | Resistor fails-open. | No voltage will be available at power controlling MOSFET gate. On-board 15 V supply will not be available. No output available at HV transformer board. | iiSC will be unable to get power from HVT board. If previously system was in injection then iiSC will get power from Universal PSB. But if previously system was in monitoring mode and capacitor bank is not charged than iiSC will have no power available. | Affected device and associated group will not be able to enter injection mode. System will keep working normally with reduced injection capability. | 3 | Over voltage. Over Temperature. Over stress due to shock or vibration. De-gradation of components. Overcurrent. Counterfeit part. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant 24 V supply to iiSC board will be provided via UPSB. | 1 | 3 | HALT. Electrical Stress Testing. Thermal Stress Testing. Vibration testing. | None. | 5 | 15 | [9 empty] | 0 |  | 6808
SV104 - 6809 |  |  |  | Any One Resistor fails-short. | No immediate effect on board. Board will keep working normally. | iiSC will be unable to get power from HVT board. If previously system was in injection then iiSC will get power from Universal PSB. But if previously system was in monitoring mode and capacitor bank is not charged than iiSC will have no power available. | System will keep working normally. | 1 | Wear-out due to extensive use. Excessive humidity. Counterfeit part. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements.. Conformal coating. Redundant 24 V supply to iiSC board will be provided via UPSB. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. Vibration testing. | None. | 5 | 5 | [11 empty] | 6809
SV104-12392 |  |  |  | More than one resistors fails-short. | Soft starting current is increased significantly consequently MOSFET power dissipation will increase that could bring failure. No output available at HV transformer board. | iiSC will be unable to get power from HVT board. If previously system was in injection then iiSC will get power from Universal PSB. But if previously system was in monitoring mode and capacitor bank is not charged than iiSC will have no power available. | Affected device and associated group will not be able to enter injection mode. System will keep working normally with reduced injection capability. | 3 | Wear-out due to extensive use. Excessive humidity. Counterfeit part. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements.. Conformal coating. Redundant 24 V supply to iiSC board will be provided via UPSB. | 1 | 3 | HALT. Electrical Stress Testing. Thermal Stress Testing. Vibration testing. | None. | 5 | 15 | [11 empty] | 12392
SV104 - 6810 | Input Power Control MOSFET. | Q6 | To turn ON/OFF power flow. | MOSFET fails-open. | Input power path will be broken. No output available at HV transformer board. | iiSC will be unable to get power from HVT board. If previously system was in injection then iiSC will get power from Universal PSB. But if previously system was in monitoring mode and capacitor bank is not charged than iiSC will have no power available. | Affected device and associated group will not be able to enter injection mode. System will keep working normally with reduced injection capability. | 3 | Overheating Mechanical stress resulting in cracked MOSFET body. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant 24 V supply to iiSC board will be provided via UPSB. | 1 | 3 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 15 | [9 empty] | 0 |  | 6810
SV104 - 6811 |  |  |  | MOSFET fails-short. | Startup circuitry will turn on permanently resulting in overheating and permanently damage to startup resistor. No output available once HV-ISO reboot. | iiSC will be unable to get power from HVT board. If previously system was in injection then iiSC will get power from Universal PSB. But if previously system was in monitoring mode and capacitor bank is not charged than iiSC will have no power available. | Affected device and associated group will not be able to enter injection mode. System will keep working normally with reduced injection capability. | 3 | Transients Overheating as a result of loose connection with heat sink Overcurrent Counterfeit part Damage during mechanical assembly of board Metallic debris stuck in between terminals | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant 24 V supply to iiSC board will be provided via UPSB. | 1 | 3 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 15 | [11 empty] | 6811
SV104 - 6812 | Over-voltage Protection Zener Diode at MOSFET Gate Side. | D31 | For gate protection of MOSFET. | Diode fails-open. | Over-voltage protection of MOSFET won't be available. No immediate effect on board in normal operations. | iiSC will be unable to get power from HVT board. If previously system was in injection then iiSC will get power from Universal PSB. But if previously system was in monitoring mode and capacitor bank is not charged than iiSC will have no power available. | System will keep working normally. | 1 | On-board fault causing higher current flow. Excessive forward current. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant 24 V supply to iiSC board will be provided via UPSB. | 2 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 10 | [9 empty] | 0 |  | 6812
SV104 - 6813 |  |  |  | Diode fails-short. | MOSFET Q6 will be turned off completely. Startup circuit will not work. No output available at HV transformer board. Board never boots up. | iiSC will be unable to get power from HVT board. If previously system was in injection then iiSC will get power from Universal PSB. But if previously system was in monitoring mode and capacitor bank is not charged than iiSC will have no power available. | Affected device and associated group will not be able to enter injection mode. System will keep working normally with reduced injection capability. | 3 | Large reverse voltage. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant 24 V supply to iiSC board will be provided via UPSB. | 2 | 6 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 30 | [11 empty] | 6813
SV104-12393 | Filtration Capacitor | C21 | To suppress noise and remove ripples | Capacitor fails-open. | No immediate effect on board. Board will keep working normally. | iiSC will be unable to get power from HVT board. If previously system was in injection then iiSC will get power from Universal PSB. But if previously system was in monitoring mode and capacitor bank is not charged than iiSC will have no power available. | System will keep working normally. | 1 | Mechanical stress. Localized heating for long time will separate end connection of capacitor. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant 24 V supply to iiSC board will be provided via UPSB. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. Vibration Testing. | None. | 5 | 5 | [11 empty] | 12393
SV104-12394 |  |  |  | Capacitor fails-short. | HVDC and 24VAUX will be shorted top ground. Startup circuit will not work. Input Fuse Will be Blown No output available at HV transformer board. | iiSC will be unable to get power from HVT board. If previously system was in injection then iiSC will get power from Universal PSB. But if previously system was in monitoring mode and capacitor bank is not charged than iiSC will have no power available. | Affected device and associated group will not be able to enter injection mode. System will keep working normally with reduced injection capability. | 3 | Wear-out due to dielectric degradation. High-voltage transients. De-gradation of components. Water ingress during humidity condition as it is film capacitor. Overvoltage | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant 24 V supply to iiSC board will be provided via UPSB. | 1 | 3 | HALT. Electrical Stress Testing. Thermal Stress Testing. Environmental Testing. | None. | 5 | 15 | [11 empty] | 12394
SV104-10995 | MOSFET resistance for Miller Capacitance | R37 | To discharge miller capacitance of MOSFET | Resistor fails-open | Abnormal Behavior of MOSFET Might turn ON/OFF abnormally. Once Board Reboots no output will be available No output available at HV transformer board | iiSC will be unable to get power from HVT board. If previously system was in injection then iiSC will get power from Universal PSB. But if previously system was in monitoring mode and capacitor bank is not charged than iiSC will have no power available. | Affected device and associated group will not be able to enter injection mode. System will keep working normally with reduced injection capability. | 3 | Over voltage. Over Temperature. Over stress due to shock or vibration. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant 24 V supply to iiSC board will be provided via UPSB. | 1 | 3 | HALT. Electrical Stress Testing. Thermal Stress Testing. Vibration testing. | None. | 5 | 15 | [11 empty] | 10995
SV104-10996 |  |  |  | Resistor fails-short | Gate and Source of Q6 will have no voltage difference so MOSFET cannot operate No output available at HV transformer board | iiSC will be unable to get power from HVT board. If previously system was in injection then iiSC will get power from Universal PSB. But if previously system was in monitoring mode and capacitor bank is not charged than iiSC will have no power available. | Affected device and associated group will not be able to enter injection mode. System will keep working normally with reduced injection capability. | 3 | Wear-out due to extensive use. Excessive humidity. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant 24 V supply to iiSC board will be provided via UPSB. | 1 | 3 | HALT. Electrical Stress Testing. Thermal Stress Testing. Vibration testing. | None. | 5 | 15 | [11 empty] | 10996
SV104 - 6814 | D21-Free wheeling diode | D21 | To protect BJT during reverse voltage condition | Diode fails-open. | No protection for BJT will be available. Reverse voltage development across BJT will damage it. No output available. | iiSC will be unable to get power from HVT board. If previously system was in injection then iiSC will get power from Universal PSB. But if previously system was in monitoring mode and capacitor bank is not charged than iiSC will have no power available. | Affected device and associated group will not be able to enter injection mode. System will keep working normally with reduced injection capability. | 3 | On-board fault causing higher current flow. Excessive forward current. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant 24 V supply to iiSC board will be provided via UPSB. | 1 | 3 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 15 | [11 empty] | 6814
SV104 - 6815 |  |  |  | Diode fails-short. | Input will appear as it is on output which will damage PWM controller and gate driver ICs permanently. No output available. | iiSC will be unable to get power from HVT board. If previously system was in injection then iiSC will get power from Universal PSB. But if previously system was in monitoring mode and capacitor bank is not charged than iiSC will have no power available. | Affected device and associated group will not be able to enter injection mode. System will keep working normally with reduced injection capability. | 3 | Large reverse voltage. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant 24 V supply to iiSC board will be provided via UPSB. | 1 | 3 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 15 | [11 empty] | 6815
SV104 - 6816 | D22-To prevent reverse power flow | D22 | To prevent reverse power flow from auxiliary to startup circuitry | Diode fails-open. | Input power path will be broken. No output available at HV transformer board. | iiSC will be unable to get power from HVT board. If previously system was in injection then iiSC will get power from Universal PSB. But if previously system was in monitoring mode and capacitor bank is not charged than iiSC will have no power available. | Affected device and associated group will not be able to enter injection mode. System will keep working normally with reduced injection capability. | 3 | On-board fault causing higher current flow. Excessive forward current. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant 24 V supply to iiSC board will be provided via UPSB. | 1 | 3 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 15 | [11 empty] | 6816
SV104 - 6817 |  |  |  | Diode fails-short. | If the board is OFF than it can not turn ON. If board is ON than reverse power will start to flow. D31 will be forward biased and as gate of Q6 is grounded than 24VAUX will also be grounded. No output available at HV transformer board. | iiSC will be unable to get power from HVT board. If previously system was in injection then iiSC will get power from Universal PSB. But if previously system was in monitoring mode and capacitor bank is not charged than iiSC will have no power available. | Affected device and associated group will not be able to enter injection mode. System will keep working normally with reduced injection capability. | 3 | Large reverse voltage. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant 24 V supply to iiSC board will be provided via UPSB. | 1 | 3 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 15 | [11 empty] | 6817
SV104 - 6818 | D27-Zener diode | D27 | To set reference voltage for BJT to regulate | Diode fails-open. | Voltage at input will appear as it is on base damaging it permanently. No output available at HV transformer board. | iiSC will be unable to get power from HVT board. If previously system was in injection then iiSC will get power from Universal PSB. But if previously system was in monitoring mode and capacitor bank is not charged than iiSC will have no power available. | Affected device and associated group will not be able to enter injection mode. System will keep working normally with reduced injection capability. | 3 | Electrical, Mechanical or environmental overstress. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant 24 V supply to iiSC board will be provided via UPSB. | 2 | 6 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 30 | [11 empty] | 6818
SV104 - 6819 |  |  |  | Diode fails-short. | BJT will not turn on. No output available at HV transformer board. | iiSC will be unable to get power from HVT board. If previously system was in injection then iiSC will get power from Universal PSB. But if previously system was in monitoring mode and capacitor bank is not charged than iiSC will have no power available. | Affected device and associated group will not be able to enter injection mode. System will keep working normally with reduced injection capability. | 3 | Excessive Temperature. Overcurrent. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant 24 V supply to iiSC board will be provided via UPSB. | 2 | 6 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 30 | [11 empty] | 6819
SV104 - 6820 | Input Power Control BJT. | Q8 | To provide regulated voltage for startup. | BJT fails-open. | Input power path will be broken. No output available at HV transformer board. | iiSC will be unable to get power from HVT board. If previously system was in injection then iiSC will get power from Universal PSB. But if previously system was in monitoring mode and capacitor bank is not charged than iiSC will have no power available. | Affected device and associated group will not be able to enter injection mode. System will keep working normally with reduced injection capability. | 3 | Melted connections due to overheating. Manufacturing defect. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant 24 V supply to iiSC board will be provided via UPSB. | 1 | 3 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 15 | [9 empty] | 0 |  | 6820
SV104 - 6821 |  |  |  | BJT fails-short. | Higher voltage at startup will damage the PWM controller and gate drivers of board. Input power path will be broken. No output available at HV transformer board. | iiSC will be unable to get power from HVT board. If previously system was in injection then iiSC will get power from Universal PSB. But if previously system was in monitoring mode and capacitor bank is not charged than iiSC will have no power available. | Affected device and associated group will not be able to enter injection mode. System will keep working normally with reduced injection capability. | 3 | Over voltage. Leaky junctions. Wear-out due to high power dissipation. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant 24 V supply to iiSC board will be provided via UPSB. | 1 | 3 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 15 | [11 empty] | 6821
SV104 - 6822 | Biasing Resistor for BJT. | R40 | To set biasing threshold for power flow controlling BJT. | Resistor fails-open. | BJT will be permanently turned OFF. Input power path will be broken. No output available at HV transformer board. | iiSC will be unable to get power from HVT board. If previously system was in injection then iiSC will get power from Universal PSB. But if previously system was in monitoring mode and capacitor bank is not charged than iiSC will have no power available. | Affected device and associated group will not be able to enter injection mode. System will keep working normally with reduced injection capability. | 3 | Over voltage. Over Temperature. Over stress due to shock or vibration. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant 24 V supply to iiSC board will be provided via UPSB. | 1 | 3 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 15 | [11 empty] | 6822
SV104 - 6823 |  |  |  | Resistor fails-short. | 24 V will be replicated at the emitter for the shorted duration, on-board ICs may get burn due to this over-voltage. BJT will eventually fail-open due to over-current. Input power path will be broken. No output available at HV transformer board. | iiSC will be unable to get power from HVT board. If previously system was in injection then iiSC will get power from Universal PSB. But if previously system was in monitoring mode and capacitor bank is not charged than iiSC will have no power available. | Affected device and associated group will not be able to enter injection mode. System will keep working normally with reduced injection capability. | 3 | Wear-out due to extensive use. Excessive humidity. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant 24 V supply to iiSC board will be provided via UPSB. | 1 | 3 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 15 | [11 empty] | 6823
SV104 - 6824 | Freewheeling Diode. |  | To provide reverser current flow path. | Diode fails-open. | No path will be available for reverse current to flow. Potential difference creation across BJT can damage the BJT. Input power path will be broken. No output available at HV transformer board. | iiSC will be unable to get power from HVT board. If previously system was in injection then iiSC will get power from Universal PSB. But if previously system was in monitoring mode and capacitor bank is not charged than iiSC will have no power available. | System will keep working normally. | 1 | Excessive forward current flow. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant 24 V supply to iiSC board will be provided via UPSB. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [11 empty] | 6824
SV104 - 6825 |  |  |  | Diode fails-short. | An emitter to collector short on BJT will cause the BJT to over-heat and may fail-open. Input power path will be broken. No output available at HV transformer board. | iiSC will be unable to get power from HVT board. If previously system was in injection then iiSC will get power from Universal PSB. But if previously system was in monitoring mode and capacitor bank is not charged than iiSC will have no power available. | System will keep working normally. | 1 | Large reverse voltage. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant 24 V supply to iiSC board will be provided via UPSB. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [9 empty] | 0 |  | 6825
SV104 - 6826 | 15 V Rail Output Side Capacitors. | C22,C19,C20 | To stable output voltage and to suppress ripples. | Capacitor fails-open. | No immediate effect on board.. | iiSC will be unable to get power from HVT board. If previously system was in injection then iiSC will get power from Universal PSB. But if previously system was in monitoring mode and capacitor bank is not charged than iiSC will have no power available. | System will keep working normally. | 1 | Mechanical stress. Localized heating for long time will separate end connection of capacitor. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant 24 V supply to iiSC board will be provided via UPSB. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [9 empty] | 0 |  | 6826
SV104 - 6827 |  |  |  | Capacitor fails-short. | 15 V power supply will be shorted to ground. On-board electronics will not be powered up. No output available at HV transformer board. | iiSC will be unable to get power from HVT board. If previously system was in injection then iiSC will get power from Universal PSB. But if previously system was in monitoring mode and capacitor bank is not charged than iiSC will have no power available. | Affected device and associated group will not be able to enter injection mode. System will keep working normally with reduced injection capability. | 3 | Wear-out due to dielectric degradation. High-voltage transients. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant 24 V supply to iiSC board will be provided via UPSB. | 1 | 3 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 15 | [9 empty] | 0 |  | 6827
SV104 - 6828 | 24 V Feedback Signal Side Resistor. | R38 | To provide 24 V sensing feedback path. | Resistor fails-open. | 15 V regulator will keep on working from input side and will not turn off. Which will heat up the resistor on MOSFET Q6 drain and will burn out eventually. No output available at HV transformer board. | iiSC will be unable to get power from HVT board. If previously system was in injection then iiSC will get power from Universal PSB. But if previously system was in monitoring mode and capacitor bank is not charged than iiSC will have no power available. | Affected device and associated group will not be able to enter injection mode. System will keep working normally with reduced injection capability. | 3 | Over voltage. Over Temperature. Over stress due to shock or vibration. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant 24 V supply to iiSC board will be provided via UPSB. | 1 | 3 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 15 | [9 empty] | 0 |  | 6828
SV104 - 6829 |  |  |  | Resistor fails-short. | Over-current will cause the resistor to eventually fail-open. 15 V regulator will keep on working from input side and will not turn off. Which will heat up the resistor on MOSFET Q6 drain and will burn out eventually. No output available at HV transformer board. | iiSC will be unable to get power from HVT board. If previously system was in injection then iiSC will get power from Universal PSB. But if previously system was in monitoring mode and capacitor bank is not charged than iiSC will have no power available. | Affected device and associated group will not be able to enter injection mode. System will keep working normally with reduced injection capability. | 3 | Wear-out due to extensive use. Excessive humidity. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant 24 V supply to iiSC board will be provided via UPSB. | 1 | 3 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 15 | [11 empty] | 6829
SV104 - 6830 | 24 V Feedback Signal Side 9 V Zener Diode. | D23 | To maintain a constant 9 V drop. To turn off the startup circuitry once full bridge auxiliary supply exceeds 9.1 V. | Diode fails-open. | 15 V regulator will keep on working from input side and will not turn off. Which will heat up the resistor on MOSFET Q6 drain and will burn out eventually. No output available at HV transformer board. | iiSC will be unable to get power from HVT board. If previously system was in injection then iiSC will get power from Universal PSB. But if previously system was in monitoring mode and capacitor bank is not charged than iiSC will have no power available. | Affected device and associated group will not be able to enter injection mode. System will keep working normally with reduced injection capability. | 3 | Electrical, Mechanical or environmental overstress. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant 24 V supply to iiSC board will be provided via UPSB. | 2 | 6 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 30 | [9 empty] | 0 |  | 6830
SV104 - 6831 |  |  |  | Diode fails-short. | Startup circuitry will be turned off before full bridge secondary is activated completely. As a result startup circuitry will keep activating and then turn off due to aux voltage. This will eventually damage the startup circuitry of board. No output available at HV transformer board. | iiSC will be unable to get power from HVT board. If previously system was in injection then iiSC will get power from Universal PSB. But if previously system was in monitoring mode and capacitor bank is not charged than iiSC will have no power available. | Affected device and associated group will not be able to enter injection mode. System will keep working normally with reduced injection capability. | 3 | Excessive Temperature. Overcurrent. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant 24 V supply to iiSC board will be provided via UPSB. | 2 | 6 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 30 | [11 empty] | 6831
SV104 - 6832 | 24 V Feedback Signal Side - R39 | R39 | Voltage divider resistor-Low side | Resistor fails-open | 15 V regulator will keep on working from input side and will not turn off. Which will heat up the resistor on MOSFET Q6 drain and will burn out eventually. No output available at HV transformer board. | iiSC will be unable to get power from HVT board. If previously system was in injection then iiSC will get power from Universal PSB. But if previously system was in monitoring mode and capacitor bank is not charged than iiSC will have no power available. | Affected device and associated group will not be able to enter injection mode. System will keep working normally with reduced injection capability. | 3 | Over voltage. Over Temperature. Over stress due to shock or vibration. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant 24 V supply to iiSC board will be provided via UPSB. | 1 | 3 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 15 | [9 empty] | 0 |  | 6832
SV104 - 6833 |  |  |  | Resistor fails-short | 15 V regulator will keep on working from input side and will not turn off. Which will heat up the resistor on MOSFET Q6 drain and will burn out eventually. No output available at HV transformer board. | iiSC will be unable to get power from HVT board. If previously system was in injection then iiSC will get power from Universal PSB. But if previously system was in monitoring mode and capacitor bank is not charged than iiSC will have no power available. | Affected device and associated group will not be able to enter injection mode. System will keep working normally with reduced injection capability. | 3 | Wear-out due to extensive use. Excessive humidity. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant 24 V supply to iiSC board will be provided via UPSB. | 1 | 3 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 15 | [11 empty] | 6833
SV104 - 6834 | 24 V Feedback Signal Side - D23 | D23 | To maintain a constant 9 V drop. To turn off the startup circuitry once full bridge auxiliary supply exceeds 9.1 V. | Diode fails-open | 15 V regulator will keep on working from input side and will not turn off. Which will heat up the resistor on MOSFET Q6 drain and will burn out eventually. No output available at HV transformer board. | iiSC will be unable to get power from HVT board. If previously system was in injection then iiSC will get power from Universal PSB. But if previously system was in monitoring mode and capacitor bank is not charged than iiSC will have no power available. | System will keep working normally. | 2 | Excessive forward current flow. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant 24 V supply to iiSC board will be provided via UPSB. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 10 | [9 empty] | 0 |  | 6834
SV104 - 6835 |  |  |  | Diode fails-short | No immediate effect on board. | iiSC will be unable to get power from HVT board. If previously system was in injection then iiSC will get power from Universal PSB. But if previously system was in monitoring mode and capacitor bank is not charged than iiSC will have no power available. | System will keep working normally. | 1 | Large reverse voltage. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant 24 V supply to iiSC board will be provided via UPSB. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [11 empty] | 6835
SV104 - 6836 | 24 V Feedback Signal Side - D24 | D24 | To prevent reverse power flow from startup circuitry | Diode fails-open | As soon as auxiliary will develop board will be disabled and power-up again and this cycle will keep repeating which will damage the startup circuitry permanently. No output available at HV transformer board. | iiSC will be unable to get power from HVT board. If previously system was in injection then iiSC will get power from Universal PSB. But if previously system was in monitoring mode and capacitor bank is not charged than iiSC will have no power available. | Affected device and associated group will not be able to enter injection mode. System will keep working normally with reduced injection capability. | 3 | Excessive forward current flow. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant 24 V supply to iiSC board will be provided via UPSB. | 1 | 3 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 15 | [11 empty] | 6836
SV104 - 6837 |  |  |  | Diode fails-short | Startup circuitry will disable itself before powering up the board. It will happen repeatedly eventually damaging the startup circuitry. No output available at HV transformer board. | iiSC will be unable to get power from HVT board. If previously system was in injection then iiSC will get power from Universal PSB. But if previously system was in monitoring mode and capacitor bank is not charged than iiSC will have no power available. | Affected device and associated group will not be able to enter injection mode. System will keep working normally with reduced injection capability. | 3 | Large reverse voltage. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant 24 V supply to iiSC board will be provided via UPSB. | 1 | 3 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 15 | [11 empty] | 6837
SV104 - 6838 | 24 V Feedback Signal Side - D26 | D26 | Overvoltage protection for MOSFET | Diode fails-open | No immediate effect on board. | iiSC will be unable to get power from HVT board. If previously system was in injection then iiSC will get power from Universal PSB. But if previously system was in monitoring mode and capacitor bank is not charged than iiSC will have no power available. | System will keep working normally. | 1 | Excessive forward current flow. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant 24 V supply to iiSC board will be provided via UPSB. | 2 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 10 | [9 empty] | 0 |  | 6838
SV104 - 6839 |  |  |  | Diode fails-short | 15 V regulator will keep on working from input side and will not turn off. Which will heat up the resistor on MOSFET Q6 drain and will burn out eventually. No output available at HV transformer board. | iiSC will be unable to get power from HVT board. If previously system was in injection then iiSC will get power from Universal PSB. But if previously system was in monitoring mode and capacitor bank is not charged than iiSC will have no power available. | Affected device and associated group will not be able to enter injection mode. System will keep working normally with reduced injection capability. | 3 | Large reverse voltage. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant 24 V supply to iiSC board will be provided via UPSB. | 2 | 6 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 30 | [11 empty] | 6839
SV104 - 6840 | 24 V Feedback Signal Side MOSFET. | Q7 | To turn OFF power flow controlling MOSFET when auxiliary voltage develops. | MOSFET fails-open. | 15 V regulator will keep on working from input side and will not turn off. Which will heat up the resistor on MOSFET Q6 drain and will burn out eventually. No output available at HV transformer board. | iiSC will be unable to get power from HVT board. If previously system was in injection then iiSC will get power from Universal PSB. But if previously system was in monitoring mode and capacitor bank is not charged than iiSC will have no power available. | Affected device and associated group will not be able to enter injection mode. System will keep working normally with reduced injection capability. | 3 | Overheating Mechanical stress resulting in cracked MOSFET body. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant 24 V supply to iiSC board will be provided via UPSB. | 1 | 3 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 15 | [9 empty] | 0 |  | 6840
SV104 - 6841 |  |  |  | MOSFET fails-short. | "Board will not power up as startup circuit will remain off. Q6 will remain permanently off. No output available at HV transformer board." | iiSC will be unable to get power from HVT board. If previously system was in injection then iiSC will get power from Universal PSB. But if previously system was in monitoring mode and capacitor bank is not charged than iiSC will have no power available. | Affected device and associated group will not be able to enter injection mode. System will keep working normally with reduced injection capability. | 3 | Transients Overheating as a result of loose connection with heat sink Overcurrent Counterfeit part Damage during mechanical assembly of board Metallic debris stuck in between terminals | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant 24 V supply to iiSC board will be provided via UPSB. | 1 | 3 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 15 | [11 empty] | 6841
SV104 - 6842 | 24 V Feedback Signal Side MOSFET.- Zener at Gate | D25 | To protect MOSFET (Q6) gate from over-voltage. | Diode fails-open. | Over-voltage protection of MOSFET won't be available. No immediate effect on board in normal operations. | iiSC will be unable to get power from HVT board. If previously system was in injection then iiSC will get power from Universal PSB. But if previously system was in monitoring mode and capacitor bank is not charged than iiSC will have no power available. | System will keep working normally. | 1 | Over voltage. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant 24 V supply to iiSC board will be provided via UPSB. | 2 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 10 | [11 empty] | 6842
SV104 - 6843 |  |  |  | Diode fails-short. | Board will not power up as startup circuit will remain off. Q6 will remain permanently off. No output available at HV transformer board. | iiSC will be unable to get power from HVT board. If previously system was in injection then iiSC will get power from Universal PSB. But if previously system was in monitoring mode and capacitor bank is not charged than iiSC will have no power available. | Affected device and associated group will not be able to enter injection mode. System will keep working normally with reduced injection capability. | 3 | On-board fault causing higher current flow. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant 24 V supply to iiSC board will be provided via UPSB. | 2 | 6 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 30 | [11 empty] | 6843
| PWM Controller | [26 empty] | 0
SV104 - 6844 | PWM Controller IC. | U1 | To provide alternate PWM pulses for full bridge gate driver. | IC output is permanently low. | No PWM will be available for half bridge driver ICs, No output available at HV transformer board. | iiSC will be unable to get power from HVT board. If previously system was in injection then iiSC will get power from Universal PSB. But if previously system was in monitoring mode and capacitor bank is not charged than iiSC will have no power available. | Affected device and associated group will not be able to enter injection mode. System will keep working normally with reduced injection capability. | 3 | Electrical Overstress. ESD. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant 24 V supply to iiSC board will be provided via UPSB. | 1 | 3 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 15 | [11 empty] | 6844
SV104 - 6845 |  |  |  | One of output is permanently high. | Output of Full Bridge circuit will be 12 V at no load. HV transformer board will have no output as soon as load is applied. | iiSC will be unable to get power from HVT board. If previously system was in injection then iiSC will get power from Universal PSB. But if previously system was in monitoring mode and capacitor bank is not charged than iiSC will have no power available. | Affected device and associated group will not be able to enter injection mode. System will keep working normally with reduced injection capability. | 3 | Electrical Overstress. ESD. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant 24 V supply to iiSC board will be provided via UPSB. | 1 | 3 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 15 | [9 empty] | 0 |  | 6845
SV104 - 6846 |  |  |  | PWM is having different duty cycle than desired. | Output of Full Bridge circuit will have different duty cycle. HV transformer board will have more or less than 24 V output. | iiSC will be unable to get power from HVT board. If previously system was in injection then iiSC will get power from Universal PSB. But if previously system was in monitoring mode and capacitor bank is not charged than iiSC will have no power available. | System will keep working normally. | 1 | Internal IC damage. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant 24 V supply to iiSC board will be provided via UPSB. | 2 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 10 | [11 empty] | 6846
SV104 - 6847 | Line Under-Voltage Lockout Voltage Divider High Side Resistor. | R1 | To turn OFF gate driver PWM in case of under-voltage. | Resistor fails-open. | PWM controller will remain off permanently. No output available. | iiSC will be unable to get power from HVT board. If previously system was in injection then iiSC will get power from Universal PSB. But if previously system was in monitoring mode and capacitor bank is not charged than iiSC will have no power available. | Affected device and associated group will not be able to enter injection mode. System will keep working normally with reduced injection capability. | 3 | Over voltage. Over Temperature. Over stress due to shock or vibration. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant 24 V supply to iiSC board will be provided via UPSB. | 1 | 3 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 15 | [11 empty] | 6847
SV104 - 6848 |  |  |  | Resistor fails-short. | UVLO pin will get damaged, No PWM will be available for half bridge driver ICs, No output available at HV transformer board. | iiSC will be unable to get power from HVT board. If previously system was in injection then iiSC will get power from Universal PSB. But if previously system was in monitoring mode and capacitor bank is not charged than iiSC will have no power available. | Affected device and associated group will not be able to enter injection mode. System will keep working normally with reduced injection capability. | 3 | Wear-out due to extensive use. Excessive humidity. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant 24 V supply to iiSC board will be provided via UPSB. | 1 | 3 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 15 | [9 empty] | 0 |  | 6848
SV104 - 6849 | Line Under-Voltage Lockout Voltage Divider Low Side Resistor. | R13 | To turn OFF gate driver PWM in case of under-voltage. | Resistor fails-open. | UVLO pin will get damaged, No PWM will be available for half bridge driver ICs, No output available at HV transformer board. | iiSC will be unable to get power from HVT board. If previously system was in injection then iiSC will get power from Universal PSB. But if previously system was in monitoring mode and capacitor bank is not charged than iiSC will have no power available. | Affected device and associated group will not be able to enter injection mode. System will keep working normally with reduced injection capability. | 3 | Over voltage. Over Temperature. Over stress due to shock or vibration. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant 24 V supply to iiSC board will be provided via UPSB. | 1 | 3 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 15 | [11 empty] | 6849
SV104 - 6850 |  |  |  | Resistor fails-short. | PWM controller will remain off permanently. No output available. | iiSC will be unable to get power from HVT board. If previously system was in injection then iiSC will get power from Universal PSB. But if previously system was in monitoring mode and capacitor bank is not charged than iiSC will have no power available. | Affected device and associated group will not be able to enter injection mode. System will keep working normally with reduced injection capability. | 3 | Wear-out due to extensive use. Excessive humidity. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant 24 V supply to iiSC board will be provided via UPSB. | 1 | 3 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 15 | [11 empty] | 6850
SV104 - 6851 | RT2 Biasing Resistor. | R14 | To control oscillator dead time. | Resistor fails-open. | Dead time between alternating PWMs will be altered (maximum). 1 PWM will be permanently high, while other will be permanently low. Output of isolation transformer will not be available. No output available at HV transformer board. | iiSC will be unable to get power from HVT board. If previously system was in injection then iiSC will get power from Universal PSB. But if previously system was in monitoring mode and capacitor bank is not charged than iiSC will have no power available. | Affected device and associated group will not be able to enter injection mode. System will keep working normally with reduced injection capability. | 3 | Over voltage. Over Temperature. Over stress due to shock or vibration. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant 24 V supply to iiSC board will be provided via UPSB. | 1 | 3 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 15 | [11 empty] | 6851
SV104 - 6852 |  |  |  | Resistor fails-short. | Dead time between alternating PWMs will be altered (maximum). 1 PWM will be permanently high, while other will be permanently low. Output of isolation transformer will not be available. No output available at HV transformer board. | iiSC will be unable to get power from HVT board. If previously system was in injection then iiSC will get power from Universal PSB. But if previously system was in monitoring mode and capacitor bank is not charged than iiSC will have no power available. | Affected device and associated group will not be able to enter injection mode. System will keep working normally with reduced injection capability. | 3 | Wear-out due to extensive use. Excessive humidity. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant 24 V supply to iiSC board will be provided via UPSB. | 1 | 3 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 15 | [11 empty] | 6852
SV104 - 6853 | RT1 Biasing Resistor. | R15 | To control oscillator maximum ON time. | Resistor fails-open. | Dead time between alternating PWMs will be altered (maximum). 1 PWM will be permanently high, while other will be permanently low. Output of isolation transformer will not be available. No output available at HV transformer board. | iiSC will be unable to get power from HVT board. If previously system was in injection then iiSC will get power from Universal PSB. But if previously system was in monitoring mode and capacitor bank is not charged than iiSC will have no power available. | Affected device and associated group will not be able to enter injection mode. System will keep working normally with reduced injection capability. | 3 | Over voltage. Over Temperature. Over stress due to shock or vibration. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant 24 V supply to iiSC board will be provided via UPSB. | 1 | 3 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 15 | [11 empty] | 6853
SV104 - 6854 |  |  |  | Resistor fails-short. | Dead time between alternating PWMs will be altered (maximum). 1 PWM will be permanently high, while other will be permanently low. Output of isolation transformer will not be available. No output available at HV transformer board. | iiSC will be unable to get power from HVT board. If previously system was in injection then iiSC will get power from Universal PSB. But if previously system was in monitoring mode and capacitor bank is not charged than iiSC will have no power available. | Affected device and associated group will not be able to enter injection mode. System will keep working normally with reduced injection capability. | 3 | Wear-out due to extensive use. Excessive humidity. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant 24 V supply to iiSC board will be provided via UPSB. | 1 | 3 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 15 | [9 empty] | 0 |  | 6854
SV104 - 6855 | Restart Timer Resistor. | R16 | To set PWM restart signal biasing. | Resistor fails-open. | Restart timer functionality will be compromised. No immediate effect on board in normal operations. | iiSC will be unable to get power from HVT board. If previously system was in injection then iiSC will get power from Universal PSB. But if previously system was in monitoring mode and capacitor bank is not charged than iiSC will have no power available. | System will keep working normally. | 1 | Over voltage. Over Temperature. Over stress due to shock or vibration. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant 24 V supply to iiSC board will be provided via UPSB. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [11 empty] | 6855
SV104 - 6856 |  |  |  | Resistor fails-short. | Restart timer functionality will be compromised. No immediate effect on board in normal operations. | iiSC will be unable to get power from HVT board. If previously system was in injection then iiSC will get power from Universal PSB. But if previously system was in monitoring mode and capacitor bank is not charged than iiSC will have no power available. | System will keep working normally. | 1 | Wear-out due to extensive use. Excessive humidity. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant 24 V supply to iiSC board will be provided via UPSB. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [9 empty] | 0 |  | 6856
SV104 - 6857 | Soft-Start Capacitor. | C10 | To provide soft-start biasing value. | Capacitor fails-open. | Soft start functionality will be compromised. No immediate effect on board in normal operations. | iiSC will be unable to get power from HVT board. If previously system was in injection then iiSC will get power from Universal PSB. But if previously system was in monitoring mode and capacitor bank is not charged than iiSC will have no power available. | System will keep working normally. | 1 | Mechanical stress. Localized heating for long time will separate end connection of capacitor. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant 24 V supply to iiSC board will be provided via UPSB. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [11 empty] | 6857
SV104 - 6858 |  |  |  | Capacitor fails-short. | PWM controller will turn off permanently. No output available for board. | iiSC will be unable to get power from HVT board. If previously system was in injection then iiSC will get power from Universal PSB. But if previously system was in monitoring mode and capacitor bank is not charged than iiSC will have no power available. | Affected device and associated group will not be able to enter injection mode. System will keep working normally with reduced injection capability. | 3 | Wear-out due to dielectric degradation. High-voltage transients. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant 24 V supply to iiSC board will be provided via UPSB. | 1 | 3 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 15 | [11 empty] | 6858
SV104 - 6859 | Ramp Control Resistor. | R12 | To provide ramp control of PWM. | Resistor fails-open. | PWM ramp will be affected. Output of Full Bridge circuit will be different than desired. HV transformer board will have more or less than 24 V output. | iiSC will be unable to get power from HVT board. If previously system was in injection then iiSC will get power from Universal PSB. But if previously system was in monitoring mode and capacitor bank is not charged than iiSC will have no power available. | System will keep working normally. | 1 | Over voltage. Over Temperature. Over stress due to shock or vibration. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant 24 V supply to iiSC board will be provided via UPSB. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [11 empty] | 6859
SV104 - 6860 |  |  |  | Resistor fails-short. | PWM ramp will be affected. Output of Full Bridge circuit will be different than desired. HV transformer board will have more or less than 24 V output. | iiSC will be unable to get power from HVT board. If previously system was in injection then iiSC will get power from Universal PSB. But if previously system was in monitoring mode and capacitor bank is not charged than iiSC will have no power available. | System will keep working normally. | 1 | Wear-out due to extensive use. Excessive humidity. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant 24 V supply to iiSC board will be provided via UPSB. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [11 empty] | 6860
SV104 - 6861 | Current Sense Signal Filtration Capacitor. | C12 | To filter the CS signal. | Capacitor fails-open. | No immediate effect. | iiSC will be unable to get power from HVT board. If previously system was in injection then iiSC will get power from Universal PSB. But if previously system was in monitoring mode and capacitor bank is not charged than iiSC will have no power available. | System will keep working normally. | 1 | Mechanical stress. Localized heating for long time will separate end connection of capacitor. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant 24 V supply to iiSC board will be provided via UPSB. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [11 empty] | 6861
SV104 - 6862 |  |  |  | Capacitor fails-short. | Capacitor will fail-open due to over-current. PWM current limiting functionality will be compromised while the capacitor remains shorted. No immediate effect on board in normal operations. | iiSC will be unable to get power from HVT board. If previously system was in injection then iiSC will get power from Universal PSB. But if previously system was in monitoring mode and capacitor bank is not charged than iiSC will have no power available. | System will keep working normally. | 1 | Wear-out due to dielectric degradation. High-voltage transients. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant 24 V supply to iiSC board will be provided via UPSB. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [9 empty] | 0 |  | 6862
SV104 - 6863 | Current Sense Capacitor. | C9 | To limit PWM current. | Capacitor fails-open. | PWM current limiting functionality will be compromised. No immediate effect on board in normal operations. | iiSC will be unable to get power from HVT board. If previously system was in injection then iiSC will get power from Universal PSB. But if previously system was in monitoring mode and capacitor bank is not charged than iiSC will have no power available. | System will keep working normally. | 1 | Mechanical stress. Localized heating for long time will separate end connection of capacitor. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant 24 V supply to iiSC board will be provided via UPSB. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [11 empty] | 6863
SV104 - 6864 |  |  |  | Capacitor fails-short. | PWM current limiting functionality will be compromised. No immediate effect on board in normal operations. | iiSC will be unable to get power from HVT board. If previously system was in injection then iiSC will get power from Universal PSB. But if previously system was in monitoring mode and capacitor bank is not charged than iiSC will have no power available. | System will keep working normally. | 1 | Wear-out due to dielectric degradation. High-voltage transients. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant 24 V supply to iiSC board will be provided via UPSB. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [9 empty] | 0 |  | 6864
SV104-12395 | Decoupling Capacitor | C11 | To Filter Noise | Capacitor fails-open. | No immediate effect on board in normal operations. | iiSC will be unable to get power from HVT board. If previously system was in injection then iiSC will get power from Universal PSB. But if previously system was in monitoring mode and capacitor bank is not charged than iiSC will have no power available. | System will keep working normally. | 1 | Mechanical stress. Localized heating for long time will separate end connection of capacitor. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant 24 V supply to iiSC board will be provided via UPSB. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. Vibration Testing. | None. | 5 | 5 | [11 empty] | 12395
SV104-12396 |  |  |  | Capacitor fails-short. | Internal Reference Voltage will be shorted to ground. PWM output will be disabled. Input Fuse Will be Blown No output available at HV transformer board. | iiSC will be unable to get power from HVT board. If previously system was in injection then iiSC will get power from Universal PSB. But if previously system was in monitoring mode and capacitor bank is not charged than iiSC will have no power available. | Affected device and associated group will not be able to enter injection mode. System will keep working normally with reduced injection capability. | 3 | Wear-out due to dielectric degradation. High-voltage transients. De-gradation of components. Water ingress during humidity condition as it is film capacitor. Overvoltage | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant 24 V supply to iiSC board will be provided via UPSB. | 1 | 3 | HALT. Electrical Stress Testing. Thermal Stress Testing. Environmental Testing. | None. | 5 | 15 | [9 empty] | 0 |  | 12396
SV104-10997 | Input Filtration Capacitance | C1 | To suppress ripples on input voltage. | Capacitor fails-open. | No immediate effect on board due to presence of multiple capacitors at different stages.. | iiSC will be unable to get power from HVT board. If previously system was in injection then iiSC will get power from Universal PSB. But if previously system was in monitoring mode and capacitor bank is not charged than iiSC will have no power available. | System will keep working normally. | 1 | Mechanical stress. Localized heating for long time will separate end connection of capacitor. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant 24 V supply to iiSC board will be provided via UPSB. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. Vibration Testing. | None. | 5 | 5 | [11 empty] | 10997
SV104-10998 |  |  |  | Capacitor fails-short. | 15V rail will get shorted to ground thus No output available at HV transformer board . | iiSC will be unable to get power from HVT board. If previously system was in injection then iiSC will get power from Universal PSB. But if previously system was in monitoring mode and capacitor bank is not charged than iiSC will have no power available. | Affected device and associated group will not be able to enter injection mode. System will keep working normally with reduced injection capability. | 3 | Wear-out due to dielectric degradation. High-voltage transients. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant 24 V supply to iiSC board will be provided via UPSB. | 1 | 3 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 15 | [9 empty] | 0 |  | 10998
SV104-10999 | Current Sense Resistance | R28 | To Sense Overcurrent | Resistor fails-open. | Overcurrent Protection will be compromised during overcurrent condition at primary. No immediate Effect in normal condition. | iiSC will be unable to get power from HVT board. If previously system was in injection then iiSC will get power from Universal PSB. But if previously system was in monitoring mode and capacitor bank is not charged than iiSC will have no power available. | System will keep working normally. | 1 | Over voltage. Over Temperature. Over stress due to shock or vibration. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant 24 V supply to iiSC board will be provided via UPSB. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [11 empty] | 10999
SV104-11000 |  |  |  | Resistor fails-short. | IC may trigger False overcurrent and disable output. No output available at HV transformer board | iiSC will be unable to get power from HVT board. If previously system was in injection then iiSC will get power from Universal PSB. But if previously system was in monitoring mode and capacitor bank is not charged than iiSC will have no power available. | Affected device and associated group will not be able to enter injection mode. System will keep working normally with reduced injection capability. | 3 | Wear-out due to extensive use. Excessive humidity. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant 24 V supply to iiSC board will be provided via UPSB. | 1 | 3 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 15 | [11 empty] | 11000
SV104 - 6865 | Output Driver Resistor. | R4,R5 | To limit gate driver current. | Resistor fails-open. | Gate driver PWM path will be broken. No output available at HV transformer board. | iiSC will be unable to get power from HVT board. If previously system was in injection then iiSC will get power from Universal PSB. But if previously system was in monitoring mode and capacitor bank is not charged than iiSC will have no power available. | Affected device and associated group will not be able to enter injection mode. System will keep working normally with reduced injection capability. | 3 | Over voltage. Over Temperature. Over stress due to shock or vibration. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant 24 V supply to iiSC board will be provided via UPSB. | 1 | 3 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 15 | [11 empty] | 6865
SV104 - 6866 |  |  |  | Resistor fails-short. | No immediate till the shorted duration. Resistor will fail-open due to over-current. Gate driver PWM path will be broken. No output available at HV transformer board. | iiSC will be unable to get power from HVT board. If previously system was in injection then iiSC will get power from Universal PSB. But if previously system was in monitoring mode and capacitor bank is not charged than iiSC will have no power available. | Affected device and associated group will not be able to enter injection mode. System will keep working normally with reduced injection capability. | 3 | Wear-out due to extensive use. Excessive humidity. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant 24 V supply to iiSC board will be provided via UPSB. | 1 | 3 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 15 | [11 empty] | 6866
| Full Bridge Circuit | [26 empty] | 0
SV104 - 6867 | Half Bridge Gate Driver IC. | U2, U3 | To provide gate driver signal for half bridge MOSFETs. | Both output are permanently low. | One half bridge section will not have output. Output of Full Bridge circuit will be 12 V at no load. HV transformer board will have no output as soon as load is applied | iiSC will be unable to get power from HVT board. If previously system was in injection then iiSC will get power from Universal PSB. But if previously system was in monitoring mode and capacitor bank is not charged than iiSC will have no power available. | Affected device and associated group will not be able to enter injection mode. System will keep working normally with reduced injection capability. | 3 | Electrical Overstress (Overvoltage). ESD. Counterfeit part. Stress or impact during assembly. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant 24 V supply to iiSC board will be provided via UPSB. | 1 | 3 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 15 | [9 empty] | 0 |  | 6867
SV104 - 6868 |  |  |  | High side output is permanently low. | Full bridge functionality will be disturbed. No output will be available at HV transformer board as soon as load is applied. | iiSC will be unable to get power from HVT board. If previously system was in injection then iiSC will get power from Universal PSB. But if previously system was in monitoring mode and capacitor bank is not charged than iiSC will have no power available. | Affected device and associated group will not be able to enter injection mode. System will keep working normally with reduced injection capability. | 3 | Electrical Overstress (Overvoltage). ESD. Counterfeit part. Stress or impact during assembly. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant 24 V supply to iiSC board will be provided via UPSB. | 1 | 3 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 15 | [11 empty] | 6868
SV104 - 6869 |  |  |  | High side output is permanently high. | One MOSFET will be permanently turned ON. During times, when low side MOSFET of same half bridge will turn ON, HV DC line get shorted will ground. Due to high current flow, power MOSFETs may get damaged. Input side fuse will burn out and prevent cascading failures. | iiSC will be unable to get power from HVT board. If previously system was in injection then iiSC will get power from Universal PSB. But if previously system was in monitoring mode and capacitor bank is not charged than iiSC will have no power available. | Affected device and associated group will not be able to enter injection mode. System will keep working normally with reduced injection capability. | 3 | Electrical Overstress (Overvoltage). ESD. Counterfeit part. Stress or impact during assembly. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant 24 V supply to iiSC board will be provided via UPSB. | 1 | 3 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 15 | [9 empty] | 0 |  | 6869
SV104 - 8905 | Half Bridge Gate Driver IC. | U2, U3 | To provide gate driver signal for half bridge MOSFETs. | Low side output is permanently low. | Full bridge functionality will be disturbed. No output will be available at HV transformer board as soon as load is applied. | iiSC will be unable to get power from HVT board. If previously system was in injection then iiSC will get power from Universal PSB. But if previously system was in monitoring mode and capacitor bank is not charged than iiSC will have no power available. | Affected device and associated group will not be able to enter injection mode. System will keep working normally with reduced injection capability. | 3 | Electrical Overstress (Overvoltage). ESD. Counterfeit part. Stress or impact during assembly. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant 24 V supply to iiSC board will be provided via UPSB. | 1 | 3 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 15 | [11 empty] | 8905
SV104 - 8906 |  |  |  | Low side output is permanently high. | During times, when high side MOSFET of same half bridge will turn ON, HV DC line get shorted with ground. Due to high current flow, power MOSFETs may get damaged. Input side fuse will burn out and prevent cascading failures. | iiSC will be unable to get power from HVT board. If previously system was in injection then iiSC will get power from Universal PSB. But if previously system was in monitoring mode and capacitor bank is not charged than iiSC will have no power available. | Affected device and associated group will not be able to enter injection mode. System will keep working normally with reduced injection capability. | 3 | Electrical Overstress (Overvoltage). ESD. Counterfeit part. Stress or impact during assembly. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant 24 V supply to iiSC board will be provided via UPSB. | 1 | 3 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 15 | [9 empty] | 0 |  | 8906
SV104 - 8907 |  |  |  | Both outputs are permanently high. | Both MOSFETs will be permanently turned ON. HV DC line will get shorted with ground. Due to high current flow, power MOSFETs may get damaged. Input side fuse will burn out and prevent cascading failures. | iiSC will be unable to get power from HVT board. If previously system was in injection then iiSC will get power from Universal PSB. But if previously system was in monitoring mode and capacitor bank is not charged than iiSC will have no power available. | Affected device and associated group will not be able to enter injection mode. System will keep working normally with reduced injection capability. | 3 | Electrical Overstress (Overvoltage). ESD. Counterfeit part. Stress or impact during assembly. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant 24 V supply to iiSC board will be provided via UPSB. | 1 | 3 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 15 | [11 empty] | 8907
SV104 - 6870 | Half Bridge Gate Driver IC - Filter Capacitor. | C4,C5 | To provide high side gate driver floating supply. | Capacitor fails-open. | Output of gate driver IC will be affected. No output available at HV transformer board. | iiSC will be unable to get power from HVT board. If previously system was in injection then iiSC will get power from Universal PSB. But if previously system was in monitoring mode and capacitor bank is not charged than iiSC will have no power available. | Affected device and associated group will not be able to enter injection mode. System will keep working normally with reduced injection capability. | 3 | Mechanical stress. Localized heating for long time will separate end connection of capacitor. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant 24 V supply to iiSC board will be provided via UPSB. | 1 | 3 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 15 | [9 empty] | 0 |  | 6870
SV104 - 6871 |  |  |  | Capacitor fails-short. | Output of gate driver IC will be affected. No output available at HV transformer board. | iiSC will be unable to get power from HVT board. If previously system was in injection then iiSC will get power from Universal PSB. But if previously system was in monitoring mode and capacitor bank is not charged than iiSC will have no power available. | Affected device and associated group will not be able to enter injection mode. System will keep working normally with reduced injection capability. | 3 | On-board fault causing higher current flow. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant 24 V supply to iiSC board will be provided via UPSB. | 1 | 3 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 15 | [11 empty] | 6871
SV104 - 6872 | Gate Driver Output Circuit - Resistor. | R7,R24,R6,R23 | To provide path between gate driver IC and gate. | Resistor fails-open. | Output path of gate driver IC will be broken for one MOSFET. Distorted square wave will be available at full bridge circuit output. HV transformer board will have lesser output than desired. | iiSC will be unable to get power from HVT board. If previously system was in injection then iiSC will get power from Universal PSB. But if previously system was in monitoring mode and capacitor bank is not charged than iiSC will have no power available. | System will keep working normally. | 1 | Over voltage. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant 24 V supply to iiSC board will be provided via UPSB. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [11 empty] | 6872
SV104 - 6873 |  |  |  | Resistor fails-short. | Over-current will cause the resistor to eventually fail-open. Output path of gate driver IC will be broken for one MOSFET. Distorted square wave will be available at full bridge circuit output. HV transformer board will have lesser output than desired. | iiSC will be unable to get power from HVT board. If previously system was in injection then iiSC will get power from Universal PSB. But if previously system was in monitoring mode and capacitor bank is not charged than iiSC will have no power available. | System will keep working normally. | 1 | Over voltage. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [9 empty] | 0 |  | 6873
SV104 - 6874 | Gate Driver Output Circuit - General Purpose Diode. | D1,D2,D3,D4 | To turn off the MOSFET quickly through low resistance path at gate. | Diode fails-open. | MOSFET will turn off through larger resistor which will result in increased switching losses. No immediate effect in case of normal operations. | iiSC will be unable to get power from HVT board. If previously system was in injection then iiSC will get power from Universal PSB. But if previously system was in monitoring mode and capacitor bank is not charged than iiSC will have no power available. | System will keep working normally. | 1 | Over voltage. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [11 empty] | 6874
SV104 - 6875 |  |  |  | Diode fail-short. | Over-current will cause the diode to eventually fail-open. MOSFET will turn off through larger resistor which will result in increased switching losses. No immediate effect in case of normal operations. | iiSC will be unable to get power from HVT board. If previously system was in injection then iiSC will get power from Universal PSB. But if previously system was in monitoring mode and capacitor bank is not charged than iiSC will have no power available. | System will keep working normally. | 1 | Over voltage. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [9 empty] | 0 |  | 6875
SV104-11001 | Gate Driver Output Circuit -Discharge Resistor. | R2,R3,R20,R21 | To provide low resistance path between gate driver IC and gate to discharge gate capacitance. | Resistor fails-open. | Gate Capacitance will discharge slowly through high resistance path thus on/off time will be disturbed Switching losses will increase. No immediate effect on board. | iiSC will be unable to get power from HVT board. If previously system was in injection then iiSC will get power from Universal PSB. But if previously system was in monitoring mode and capacitor bank is not charged than iiSC will have no power available. | System will keep working normally. | 1 | Over voltage. Over Temperature. Over stress due to shock or vibration. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [11 empty] | 11001
SV104-11002 |  |  |  | Resistor fails-short. | Switching losses will increase. No immediate effect on board. | iiSC will be unable to get power from HVT board. If previously system was in injection then iiSC will get power from Universal PSB. But if previously system was in monitoring mode and capacitor bank is not charged than iiSC will have no power available. | System will keep working normally. | 1 | Wear-out due to extensive use. Excessive humidity. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [11 empty] | 11002
SV104-11003 | MOSFET resistance for Miller Capacitance | R10,R27,R11,R26 | To discharge capacitance between all terminals of MOSFET | Resistor fails-open | Abnormal Behavior of MOSFET Might turn ON/OFF abnormally and can damage board. No output available at HV transformer board | iiSC will be unable to get power from HVT board. If previously system was in injection then iiSC will get power from Universal PSB. But if previously system was in monitoring mode and capacitor bank is not charged than iiSC will have no power available. | Affected device and associated group will not be able to enter injection mode. System will keep working normally with reduced injection capability. | 3 | Over voltage. Over Temperature. Over stress due to shock or vibration. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 3 | HALT. Electrical Stress Testing. Thermal Stress Testing. Vibration testing. | None. | 5 | 15 | [9 empty] | 0 |  | 11003
SV104-11004 |  |  |  | Resistor fails-short | Gate and Source of MOSFET will have no voltage difference so MOSFET cannot operate No output available at HV transformer board | iiSC will be unable to get power from HVT board. If previously system was in injection then iiSC will get power from Universal PSB. But if previously system was in monitoring mode and capacitor bank is not charged than iiSC will have no power available. | Affected device and associated group will not be able to enter injection mode. System will keep working normally with reduced injection capability. | 3 | Wear-out due to extensive use. Excessive humidity. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 3 | HALT. Electrical Stress Testing. Thermal Stress Testing. Vibration testing. | None. | 5 | 15 | [11 empty] | 11004
SV104-11005 | Half Bridge Gate Driver IC - High Side Supply Capacitor. | C7,C15,C16,C8 | To provide high side supply and to ensure bootstrapping in order to operate MOSFET. | One Capacitor fails-open. | No immediate effect as the parallel capacitor will be available and will make sure that MOSFET works properly | iiSC will be unable to get power from HVT board. If previously system was in injection then iiSC will get power from Universal PSB. But if previously system was in monitoring mode and capacitor bank is not charged than iiSC will have no power available. | System will keep working normally. | 1 | Mechanical stress. Localized heating for long time will separate end connection of capacitor. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [9 empty] | 0 |  | 11005
SV104-11006 |  |  |  | Both Capacitors fails-open. | MOSFET Cannot operate properly No output available at HV transformer board | iiSC will be unable to get power from HVT board. If previously system was in injection then iiSC will get power from Universal PSB. But if previously system was in monitoring mode and capacitor bank is not charged than iiSC will have no power available. | Affected device and associated group will not be able to enter injection mode. System will keep working normally with reduced injection capability. | 3 | Mechanical stress. Localized heating for long time will separate end connection of capacitor. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 3 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 15 | [11 empty] | 11006
SV104-11007 |  |  |  | Capacitor fails-short. | MOSFET Cannot operate properly IC may get damaged No output available at HV transformer board | iiSC will be unable to get power from HVT board. If previously system was in injection then iiSC will get power from Universal PSB. But if previously system was in monitoring mode and capacitor bank is not charged than iiSC will have no power available. | Affected device and associated group will not be able to enter injection mode. System will keep working normally with reduced injection capability. | 3 | Wear-out due to dielectric degradation. High-voltage transients. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 3 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 15 | [11 empty] | 11007
SV104 - 6876 | Full Bridge Circuit - MOSFET | Q1,Q2,Q3,Q4 | To convert HV DC to HV AC signal. | MOSFET fails-open. | Distorted square wave will be available at full bridge circuit output. HV transformer board will have lesser output than desired. | iiSC will be unable to get power from HVT board. If previously system was in injection then iiSC will get power from Universal PSB. But if previously system was in monitoring mode and capacitor bank is not charged than iiSC will have no power available. | System will keep working normally. | 1 | Overheating Mechanical stress resulting in cracked MOSFET body. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [9 empty] | 0 |  | 6876
SV104 - 6877 |  |  |  | MOSFET fails-short. | No voltage will be available at transformer output, for the shorted duration. No output available at HV transformer board. | iiSC will be unable to get power from HVT board. If previously system was in injection then iiSC will get power from Universal PSB. But if previously system was in monitoring mode and capacitor bank is not charged than iiSC will have no power available. | Affected device and associated group will not be able to enter injection mode. System will keep working normally with reduced injection capability. | 3 | Transients Overheating as a result of loose connection with heat sink Overcurrent Counterfeit part Damage during mechanical assembly of board Metallic debris stuck in between terminals | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant 24 V supply to iiSC board will be provided via UPSB. | 1 | 3 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 15 | [11 empty] | 6877
SV104-11008 | Gate Driver Output Circuit -Pull Down resistance. | R29,R8 | To provide current sense signal to controller | One Resistor fails-open. | Current over limit value will decrease down to half. No immediate affect in normal condition but in case of overloaded condition current limit will be activated early. | iiSC will be unable to get power from HVT board. If previously system was in injection then iiSC will get power from Universal PSB. But if previously system was in monitoring mode and capacitor bank is not charged than iiSC will have no power available. | System will keep working normally. | 1 | Over voltage. Over Temperature. Over stress due to shock or vibration. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant 24 V supply to iiSC board will be provided via UPSB. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [11 empty] | 11008
SV104-11009 |  |  |  | Both Resistor fails-open. | Full bridge circuit ground connection will be disconnected No output available at HV transformer board | iiSC will be unable to get power from HVT board. If previously system was in injection then iiSC will get power from Universal PSB. But if previously system was in monitoring mode and capacitor bank is not charged than iiSC will have no power available. | Affected device and associated group will not be able to enter injection mode. System will keep working normally with reduced injection capability. | 3 | Over voltage. Over Temperature. Over stress due to shock or vibration. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant 24 V supply to iiSC board will be provided via UPSB. | 1 | 3 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 15 | [11 empty] | 11009
SV104-11010 |  |  |  | Resistor fails-short. | No immediate effect in case of normal operations. Overcurrent protection will not be available. | iiSC will be unable to get power from HVT board. If previously system was in injection then iiSC will get power from Universal PSB. But if previously system was in monitoring mode and capacitor bank is not charged than iiSC will have no power available. | System will keep working normally. | 1 | Wear-out due to extensive use. Excessive humidity. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant 24 V supply to iiSC board will be provided via UPSB. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [9 empty] | 0 |  | 11010
SV104 - 6878 | HV Isolation Transformer | P113720 | To step down 400 V AC to 24 V AC. | Primary winding fails-open. | No voltage will be available at transformer output. No output available at HV transformer board. | iiSC will be unable to get power from HVT board. If previously system was in injection then iiSC will get power from Universal PSB. But if previously system was in monitoring mode and capacitor bank is not charged than iiSC will have no power available. | Affected device and associated group will not be able to enter injection mode. System will keep working normally with reduced injection capability. | 3 | High operating temperature. Overloading. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant 24 V supply to iiSC board will be provided via UPSB. | 1 | 3 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 15 | [11 empty] | 6878
SV104 - 6879 |  |  |  | Secondary winding fails-open. | No output available at HV transformer board. | iiSC will be unable to get power from HVT board. If previously system was in injection then iiSC will get power from Universal PSB. But if previously system was in monitoring mode and capacitor bank is not charged than iiSC will have no power available. | Affected device and associated group will not be able to enter injection mode. System will keep working normally with reduced injection capability. | 3 | High operating temperature. Overloading. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant 24 V supply to iiSC board will be provided via UPSB. | 1 | 3 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 15 | [9 empty] | 0 |  | 6879
SV104 - 6880 |  |  |  | Core degradation. | Output voltage will be less than desired value. | iiSC will be unable to get power from HVT board. If previously system was in injection then iiSC will get power from Universal PSB. But if previously system was in monitoring mode and capacitor bank is not charged than iiSC will have no power available. | System will keep working normally. | 1 | Over voltage. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [9 empty] | 0 |  | 6880
SV104 - 6881 |  |  |  | Winding insulation melting. | Turn ratio of transformer will be affected. Output voltage will be less than desired value. | iiSC will be unable to get power from HVT board. If previously system was in injection then iiSC will get power from Universal PSB. But if previously system was in monitoring mode and capacitor bank is not charged than iiSC will have no power available. | System will keep working normally. | 1 | Over voltage. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [11 empty] | 6881
SV104 - 6882 |  |  |  | Isolation Failure. | For MVAR on lowest potential, isolation of 1kV will be enough to keep the board working. For MVAR on highest potential if the failure causes the isolation of less than 5.6 kV RMS then the board will get damaged. One of the MVAR will not be operational. | iiSC will be unable to get power from HVT board. If previously system was in injection then iiSC will get power from Universal PSB. But if previously system was in monitoring mode and capacitor bank is not charged than iiSC will have no power available. | Affected device and associated group will not be able to enter injection mode. System will keep working normally with reduced injection capability. | 4 | Temperature cycling. Manufacturing Deficiency. Vibration. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 4 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 20 | [9 empty] | 0 |  | 6882
SV104 - 6883 |  |  |  | Auxiliary winding failure(Open) | No auxiliary voltage will be available. Startup circuit will not shutdown eventually burning out. No output will be available for HV-ISO board | iiSC will be unable to get power from HVT board. If previously system was in injection then iiSC will get power from Universal PSB. But if previously system was in monitoring mode and capacitor bank is not charged than iiSC will have no power available. | Affected device and associated group will not be able to enter injection mode. System will keep working normally with reduced injection capability. | 3 | Over voltage. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 3 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 15 | [11 empty] | 6883
SV104 - 6884 |  |  |  | Post insulator fails | For MVAR on lowest potential, isolation of 1kV will be enough to keep the board working. For MVAR on highest potential if the failure causes the isolation of less than 5.6 kV RMS then the board will get damaged. One of the MVAR will not be operational. | iiSC will be unable to get power from HVT board. If previously system was in injection then iiSC will get power from Universal PSB. But if previously system was in monitoring mode and capacitor bank is not charged than iiSC will have no power available. | Affected device and associated group will not be able to enter injection mode. System will keep working normally with reduced injection capability. | 4 | Corrosion. Manufacturing Deficiency. Vibration. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 4 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 20 | [11 empty] | 6884
SV104 - 6885 |  |  |  | Potting crack or physical damage | Partial discharge will start resulting in degradation of isolation barrier with the time. Eventually degradation will reach to a level where failure will occur and iiSC board will get damaged. One of the MVAR will not be operational. | iiSC will be unable to get power from HVT board. If previously system was in injection then iiSC will get power from Universal PSB. But if previously system was in monitoring mode and capacitor bank is not charged than iiSC will have no power available. | Affected device and associated group will not be able to enter injection mode. System will keep working normally with reduced injection capability. | 4 | Corrosion. Manufacturing Deficiency. Vibration. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 4 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 20 | [11 empty] | 6885
SV104 - 6886 | HV Isolation Transformer - output Side Full Rectifier - Diode | D5,D6,D8 | To convert 24 V AC to 24 V DC. | Diode fails-open. | Output cut to half if half side is working. | iiSC will be unable to get power from HVT board. If previously system was in injection then iiSC will get power from Universal PSB. But if previously system was in monitoring mode and capacitor bank is not charged than iiSC will have no power available. | Affected device and associated group will not be able to enter injection mode. System will keep working normally with reduced injection capability. | 3 | On-board fault causing higher current flow. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant 24 V supply to iiSC board will be provided via UPSB. | 1 | 3 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 15 | [11 empty] | 6886
SV104 - 6887 |  |  |  | Diode fails-short. | Secondary winding will get shorted if any diode fails-short. As a result of shortage, excessive amount of current will flow damaging two diodes permanently. Diodes will eventually get open and no output will be available | iiSC will be unable to get power from HVT board. If previously system was in injection then iiSC will get power from Universal PSB. But if previously system was in monitoring mode and capacitor bank is not charged than iiSC will have no power available. | Affected device and associated group will not be able to enter injection mode. System will keep working normally with reduced injection capability. | 3 | On-board fault causing higher current flow. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant 24 V supply to iiSC board will be provided via UPSB. | 1 | 3 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 15 | [9 empty] | 0 |  | 6887
SV104 - 5229 | Output Side Capacitor. | C13,C14 | To suppress output side ripples and to provide filtration. | Capacitor fails-open. | Output voltage may have ripples. No immediate effect on HV transformer board output. | iiSC will be unable to get power from HVT board. If previously system was in injection then iiSC will get power from Universal PSB. But if previously system was in monitoring mode and capacitor bank is not charged than iiSC will have no power available. | System will keep working normally. | 1 | Mechanical stress. Localized heating for long time will separate end connection of capacitor. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant 24 V supply to iiSC board will be provided via UPSB. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [9 empty] | 0 |  | 5229
SV104 - 5230 |  |  |  | Capacitor fails-short. | No voltage available at the output for the shorted duration. | iiSC will be unable to get power from HVT board. If previously system was in injection then iiSC will get power from Universal PSB. But if previously system was in monitoring mode and capacitor bank is not charged than iiSC will have no power available. | Affected device and associated group will not be able to enter injection mode. System will keep working normally with reduced injection capability. | 3 | Wear-out due to dielectric degradation. High-voltage transients. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant 24 V supply to iiSC board will be provided via UPSB. | 1 | 3 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 15 | [11 empty] | 5230
SV104 - 6888 | HV Isolation Transformer - Feedback Side Full Rectifier - Diode | D15,D16,D19,D20 | To convert 24 V AC to 24 V DC for feedback. | Diode fails-open. | Output cut to half if half side is working. | iiSC will be unable to get power from HVT board. If previously system was in injection then iiSC will get power from Universal PSB. But if previously system was in monitoring mode and capacitor bank is not charged than iiSC will have no power available. | Affected device and associated group will not be able to enter injection mode. System will keep working normally with reduced injection capability. | 3 | On-board fault causing higher current flow. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant 24 V supply to iiSC board will be provided via UPSB. | 1 | 3 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 15 | [11 empty] | 6888
SV104 - 6889 |  |  |  | Diode fails-short. | Auxiliary winding will get shorted if any diode fails-short. As a result of shortage, excessive amount of current will flow damaging two diodes permanently. Diodes will eventually get open and no output will be available. | iiSC will be unable to get power from HVT board. If previously system was in injection then iiSC will get power from Universal PSB. But if previously system was in monitoring mode and capacitor bank is not charged than iiSC will have no power available. | Affected device and associated group will not be able to enter injection mode. System will keep working normally with reduced injection capability. | 3 | On-board fault causing higher current flow. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant 24 V supply to iiSC board will be provided via UPSB. | 1 | 3 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 15 | [11 empty] | 6889
SV104 - 6890 | Output Side Capacitor. | C17,C18 | To suppress output side ripples and to provide filtration. | Capacitor fails-open. | Output voltage may have ripples. No immediate effect on HV transformer board output. | iiSC will be unable to get power from HVT board. If previously system was in injection then iiSC will get power from Universal PSB. But if previously system was in monitoring mode and capacitor bank is not charged than iiSC will have no power available. | System will keep working normally. | 1 | Mechanical stress. Localized heating for long time will separate end connection of capacitor. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant 24 V supply to iiSC board will be provided via UPSB. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [11 empty] | 6890
SV104 - 6891 |  |  |  | Capacitor fails-short. | No voltage available at the output for the shorted duration. | iiSC will be unable to get power from HVT board. If previously system was in injection then iiSC will get power from Universal PSB. But if previously system was in monitoring mode and capacitor bank is not charged than iiSC will have no power available. | Affected device and associated group will not be able to enter injection mode. System will keep working normally with reduced injection capability. | 3 | On-board fault causing higher current flow. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant 24 V supply to iiSC board will be provided via UPSB. | 1 | 3 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 15 | [11 empty] | 6891
SV104-11011 | Current Limiting resistance for LED (D9) | R44 | To limit current through the LED (D9) | Resistor fails-open | LED indication functionality will be compromised No immediate effect on HV transformer board output. | iiSC will be unable to get power from HVT board. If previously system was in injection then iiSC will get power from Universal PSB. But if previously system was in monitoring mode and capacitor bank is not charged than iiSC will have no power available. | System will keep working normally. | 1 | Over voltage. Over Temperature. Over stress due to shock or vibration. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant 24 V supply to iiSC board will be provided via UPSB. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. Vibration testing. | None. | 5 | 5 | [11 empty] | 11011
SV104-11012 |  |  |  | Resistor fails-short | LED indication functionality will be compromised No immediate effect on HV transformer board output. | iiSC will be unable to get power from HVT board. If previously system was in injection then iiSC will get power from Universal PSB. But if previously system was in monitoring mode and capacitor bank is not charged than iiSC will have no power available. | System will keep working normally. | 1 | Wear-out due to extensive use. Excessive humidity. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant 24 V supply to iiSC board will be provided via UPSB. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. Vibration testing. | None. | 5 | 5 | [11 empty] | 11012
SV104-11013 | LED for status indication of voltage produced | D9 | Visual indication for board output status | Diode fails-open | LED indication functionality will be compromised No immediate effect on HV transformer board output. | iiSC will be unable to get power from HVT board. If previously system was in injection then iiSC will get power from Universal PSB. But if previously system was in monitoring mode and capacitor bank is not charged than iiSC will have no power available. | System will keep working normally. | 1 | Over voltage. Over Temperature. Over stress due to shock or vibration. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant 24 V supply to iiSC board will be provided via UPSB. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. Vibration testing. | None. | 5 | 5 | [11 empty] | 11013
SV104-11014 |  |  |  | Diode fails-short | LED indication functionality will be compromised No immediate effect on HV transformer board output. | iiSC will be unable to get power from HVT board. If previously system was in injection then iiSC will get power from Universal PSB. But if previously system was in monitoring mode and capacitor bank is not charged than iiSC will have no power available. | System will keep working normally. | 1 | Wear-out due to extensive use. Excessive humidity. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant 24 V supply to iiSC board will be provided via UPSB. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. Vibration testing. | None. | 5 | 5 | [11 empty] | 11014
SV104-11015 | Load at output | R42,R43 | To keep open load voltage within a range | Resistor fails-open | No immediate effect on board. | iiSC will be unable to get power from HVT board. If previously system was in injection then iiSC will get power from Universal PSB. But if previously system was in monitoring mode and capacitor bank is not charged than iiSC will have no power available. | System will keep working normally. | 1 | Over voltage. Over Temperature. Over stress due to shock or vibration. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant 24 V supply to iiSC board will be provided via UPSB. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. Vibration testing. | None. | 5 | 5 | [9 empty] | 0 |  | 11015
SV104-11016 |  |  |  | Resistor fails-short | 24V supply will be shorted out to ground. Resistance will eventually fail open due to over current. No output available at HV transformer board | iiSC will be unable to get power from HVT board. If previously system was in injection then iiSC will get power from Universal PSB. But if previously system was in monitoring mode and capacitor bank is not charged than iiSC will have no power available. | Affected device and associated group will not be able to enter injection mode. System will keep working normally with reduced injection capability. | 3 | Wear-out due to extensive use. Excessive humidity. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant 24 V supply to iiSC board will be provided via UPSB. | 1 | 3 | HALT. Electrical Stress Testing. Thermal Stress Testing. Vibration testing. | None. | 5 | 15 | [11 empty] | 11016
SV104-11427 | Secondary Winding Connector | J2 | Secondary of transformer | Connector Disconnected by external Force. | Secondary winding will be opened. No output available at HV transformer board. | iiSC will be unable to get power from HVT board. If previously system was in injection then iiSC will get power from Universal PSB. But if previously system was in monitoring mode and capacitor bank is not charged than iiSC will have no power available. | Affected device and associated group will not be able to enter injection mode. System will keep working normally with reduced injection capability. | 3 | Open Connections due to vibrations, mis-handling or mechanical stress. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 3 | HALT. Electrical Stress Testing. Thermal Stress Testing. Vibration Testing. | None. | 5 | 15 | [11 empty] | 11427
SV104-11428 |  |  |  | Connector Burned out | Due to sparking connector will heat up and eventually burnout No output available at HV transformer board. | iiSC will be unable to get power from HVT board. If previously system was in injection then iiSC will get power from Universal PSB. But if previously system was in monitoring mode and capacitor bank is not charged than iiSC will have no power available. | Affected device and associated group will not be able to enter injection mode. System will keep working normally with reduced injection capability. | 3 | Connection Loose or Sparking at terminals Open Connections due to vibrations, mis-handling or mechanical stress. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 3 | HALT. Electrical Stress Testing. Thermal Stress Testing. Vibration Testing. | None. | 5 | 15 | [11 empty] | 11428
SV104-11429 | Low voltage DC output Connector | J4 | Output of HVT board | Connector Disconnected by external Force. | Output path will be broken. No output available at HV transformer board. | iiSC will be unable to get power from HVT board. If previously system was in injection then iiSC will get power from Universal PSB. But if previously system was in monitoring mode and capacitor bank is not charged than iiSC will have no power available. | Affected device and associated group will not be able to enter injection mode. System will keep working normally with reduced injection capability. | 3 | Open Connections due to vibrations, mis-handling or mechanical stress. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 3 | HALT. Electrical Stress Testing. Thermal Stress Testing. Vibration Testing. | None. | 5 | 15 | [9 empty] | 0 |  | 11429
SV104-11430 |  |  |  | Connector Burned out | Due to sparking connector will heat up and eventually burnout Output path will be broken. No output available at HV transformer board. | iiSC will be unable to get power from HVT board. If previously system was in injection then iiSC will get power from Universal PSB. But if previously system was in monitoring mode and capacitor bank is not charged than iiSC will have no power available. | Affected device and associated group will not be able to enter injection mode. System will keep working normally with reduced injection capability. | 3 | Connection Loose or Sparking at terminals Open Connections due to vibrations, mis-handling or mechanical stress. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 3 | HALT. Electrical Stress Testing. Thermal Stress Testing. Vibration Testing. | None. | 5 | 15 | [11 empty] | 11430
SV104-11431 | Auxiliary winding Connector | J6 | Auxiliary winding of transformer for 24AUX | Connector Disconnected by external Force. | 24AUX path will be broken. Startup circuitry will turn on permanently resulting in overheating and permanently damage to startup resistor. No output available once HV-ISO reboot. | iiSC will be unable to get power from HVT board. If previously system was in injection then iiSC will get power from Universal PSB. But if previously system was in monitoring mode and capacitor bank is not charged than iiSC will have no power available. | Affected device and associated group will not be able to enter injection mode. System will keep working normally with reduced injection capability. | 3 | Open Connections due to vibrations, mis-handling or mechanical stress. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 3 | HALT. Electrical Stress Testing. Thermal Stress Testing. Vibration Testing. | None. | 5 | 15 | [9 empty] | 0 |  | 11431
SV104-11432 |  |  |  | Connector Burned out | Due to sparking connector will heat up and eventually burnout 24AUX path will be broken. Startup circuitry will turn on permanently resulting in overheating and permanently damage to startup resistor. No output available once HV-ISO reboot. | iiSC will be unable to get power from HVT board. If previously system was in injection then iiSC will get power from Universal PSB. But if previously system was in monitoring mode and capacitor bank is not charged than iiSC will have no power available. | Affected device and associated group will not be able to enter injection mode. System will keep working normally with reduced injection capability. | 3 | Connection Loose or Sparking at terminals Open Connections due to vibrations, mis-handling or mechanical stress. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 3 | HALT. Electrical Stress Testing. Thermal Stress Testing. Vibration Testing. | None. | 5 | 15 | [11 empty] | 11432
SV104-11433 | Primary winding of transformer | J1,J5 | primary winding of transformer | Connector Disconnected by external Force. | No voltage will be available at transformer output. No output available at HV transformer board. | iiSC will be unable to get power from HVT board. If previously system was in injection then iiSC will get power from Universal PSB. But if previously system was in monitoring mode and capacitor bank is not charged than iiSC will have no power available. | Affected device and associated group will not be able to enter injection mode. System will keep working normally with reduced injection capability. | 3 | Open Connections due to vibrations, mis-handling or mechanical stress. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 3 | HALT. Electrical Stress Testing. Thermal Stress Testing. Vibration Testing. | None. | 5 | 15 | [9 empty] | 0 |  | 11433
SV104-11434 |  |  |  | Connector Burned out | Due to sparking connector will heat up and eventually burnout No voltage will be available at transformer output. No output available at HV transformer board. | iiSC will be unable to get power from HVT board. If previously system was in injection then iiSC will get power from Universal PSB. But if previously system was in monitoring mode and capacitor bank is not charged than iiSC will have no power available. | Affected device and associated group will not be able to enter injection mode. System will keep working normally with reduced injection capability. | 3 | Connection Loose or Sparking at terminals Open Connections due to vibrations, mis-handling or mechanical stress. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 3 | HALT. Electrical Stress Testing. Thermal Stress Testing. Vibration Testing. | None. | 5 | 15 | [11 empty] | 11434
SV104 - 6892 | Heat Sink | HS1,HS2,HS3,HS4,HS5,HS6,HS7,HS8. | To provide cooling functionality for power components. | Loose connection between heat sink and power component. | Affected component will face high temperature rise during nominal current operations. Power component may get damaged causing HV transformer board output voltage to drop. | iiSC will be unable to get power from HVT board. If previously system was in injection then iiSC will get power from Universal PSB. But if previously system was in monitoring mode and capacitor bank is not charged than iiSC will have no power available. | Affected device and associated group will not be able to enter injection mode. System will keep working normally with reduced injection capability. | 3 | On-board fault causing higher current flow. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant 24 V supply to iiSC board will be provided via UPSB. | 1 | 3 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 15 | [9 empty] | 0 |  | 6892
| HV Transformer Board for 1 MVAr (with CLB Option) | [26 empty] | 0
| 15 V On-Board Supply | [26 empty] | 0
SV104 - 6893 | Input Side TRIACs. |  | Reverse polarity protection. | TRIAC fails-open. | No immediate effect. Parallel TRIAC available for alternate path. | Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | On-board fault causing higher current flow. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [11 empty] | 6893
SV104 - 6894 |  |  |  | TRIAC fails-short. | Reverse polarity protection will be compromised during shortage. | Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | On-board fault causing higher current flow. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [9 empty] | 0 |  | 6894
SV104 - 6895 |  |  |  | Both TRIACs fail-short | Reverse polarity protection will be compromised during shortage. | Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | On-board fault causing higher current flow. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 10 | [11 empty] | 6895
SV104 - 6896 |  |  |  | Both TRIACs fail-open. | Reverse polarity protection will be compromised during shortage. | Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | On-board fault causing higher current flow. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 10 | [11 empty] | 6896
SV104 - 6897 | Input Side Fuse. |  | To cut-off supply in case of over-current. | Fuse fails-open. | Input power path will be broken. No output available at HV transformer board. | iiSC will be unable to get power from HVT board, but will get power from Universal PSB. Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | On-board fault causing higher current flow. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [11 empty] | 6897
SV104 - 6898 | Input Side Filter Capacitors. |  | To suppress ripples on input voltage. To store energy for power demand. | Capacitor fails-open. | Input supply ripples may cause distorted output supply. No immediate effect on board.. | Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | Over voltage. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [9 empty] | 0 |  | 6898
SV104 - 6899 |  |  |  | Capacitor fails-short. | Overcurrent will cause the capacitor to eventually fail-open. No output available at HV transformer board till capacitor remains shorted. Input supply ripples may cause distorted output supply. No immediate effect on board.. | Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | Over voltage. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [11 empty] | 6899
SV104 - 6900 | Low Voltage Detection Zener Diode. |  | To set under-voltage lockout threshold. | Diode fails-open. | No voltage will be available at power controlling MOSFET gate. On-board 15 V supply will not be available. No output available at HV transformer board. | iiSC will be unable to get power from HVT board, but will get power from Universal PSB. Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | On-board fault causing higher current flow. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [11 empty] | 6900
SV104 - 6901 |  |  |  | Diode fails-short.. | Resistor in series will se an increased voltage drop, which may cause them to heat and burn in worst. Diode will fail-open due to over-current. No voltage will be available at power controlling MOSFET gate. On-board 15 V supply will not be available. No output available at HV transformer board. | iiSC will be unable to get power from HVT board, but will get power from Universal PSB. Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | On-board fault causing higher current flow. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [11 empty] | 6901
SV104 - 6902 | Input Side Voltage Divider Resistor. |  | To step down voltage. | Resistor fails-open. | No voltage will be available at power controlling MOSFET gate. On-board 15 V supply will not be available. No output available at HV transformer board. | iiSC will be unable to get power from HVT board, but will get power from Universal PSB. Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | On-board fault causing higher current flow. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [11 empty] | 6902
SV104 - 6903 |  |  |  | Resistor fails-short. | Remaining series resistors will see an increased voltage drop for the shorted duration. Resistor will fail-open due to over-current. No voltage will be available at power controlling MOSFET gate. On-board 15 V supply will not be available. No output available at HV transformer board. | iiSC will be unable to get power from HVT board, but will get power from Universal PSB. Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | On-board fault causing higher current flow. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [9 empty] | 0 |  | 6903
SV104 - 6904 | Input Power Control MOSFET. |  | To turn ON/OFF power flow. | MOSFET fails-open. | Input power path will be broken. No output available at HV transformer board. | iiSC will be unable to get power from HVT board, but will get power from Universal PSB. Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | On-board fault causing higher current flow. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [9 empty] | 0 |  | 6904
SV104 - 6905 |  |  |  | MOSFET fails-short. | Over-current will eventually cause the MOSFET to fail-open. Input power path will be broken. No output available at HV transformer board. | iiSC will be unable to get power from HVT board, but will get power from Universal PSB. Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | On-board fault causing higher current flow. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [9 empty] | 0 |  | 6905
SV104 - 6906 | Over-voltage Protection Zener Diode at MOSFET Gate Side. |  | To cutoff supply in case of over-voltage. | Diode fails-open. | Over-voltage protection of MOSFET won't be available. No immediate effect on board in normal operations. | Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Over voltage. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 10 | [9 empty] | 0 |  | 6906
SV104 - 6907 |  |  |  | Diode fails-short. | Over-current will cause the diode to eventually fail-open. For the shorted duration, Input power path will be broken. No output available at HV transformer board. | iiSC will be unable to get power from HVT board, but will get power from Universal PSB. Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | On-board fault causing higher current flow. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [11 empty] | 6907
SV104 - 6908 | Input Power Control BJT. |  | To provide controlled power flow path. | BJT fails-open. | Input power path will be broken. No output available at HV transformer board. | iiSC will be unable to get power from HVT board, but will get power from Universal PSB. Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | On-board fault causing higher current flow. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [9 empty] | 0 |  | 6908
SV104 - 6909 |  |  |  | BJT fails-short. | Over-current will cause the BJT to eventually fail-open. Input power path will be broken. No output available at HV transformer board. | iiSC will be unable to get power from HVT board, but will get power from Universal PSB. Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | On-board fault causing higher current flow. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [11 empty] | 6909
SV104 - 6910 | Biasing Resistor for BJT. |  | To set biasing threshold for power flow controlling BJT. | Resistor fails-open. | BJT will be permanently turned OFF. Input power path will be broken. No output available at HV transformer board. | iiSC will be unable to get power from HVT board, but will get power from Universal PSB. Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | On-board fault causing higher current flow. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [9 empty] | 0 |  | 6910
SV104 - 6911 |  |  |  | Resistor fails-short. | 24 V will be replicated at the emitter for the shorted duration, on-board ICs may get burn due to this over-voltage. BJT will eventually fail-open due to over-current. Input power path will be broken. No output available at HV transformer board. | iiSC will be unable to get power from HVT board, but will get power from Universal PSB. Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | On-board fault causing higher current flow. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [11 empty] | 6911
SV104 - 6912 | Freewheeling Diode. |  | To provide reverser current flow path. | Diode fails-open. | No path will be available for reverse current to flow. Potential difference creation across BJT can damage the BJT. Input power path will be broken. No output available at HV transformer board. | iiSC will be unable to get power from HVT board, but will get power from Universal PSB. Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | On-board fault causing higher current flow. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [9 empty] | 0 |  | 6912
SV104 - 6913 |  |  |  | Diode fails-short. | An emitter to collector short on BJT will cause the BJT to over-heat and may fail-open. Input power path will be broken. No output available at HV transformer board. | iiSC will be unable to get power from HVT board, but will get power from Universal PSB. Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | On-board fault causing higher current flow. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [11 empty] | 6913
SV104 - 6914 | 15 V Rail Output Side Capacitors. |  | To stable output voltage and to suppress ripples. | Capacitor fails-open. | No immediate effect on board.. | Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | Over voltage. De-gradation of components. | Using enough filtration capacitors at different levels. Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [11 empty] | 6914
SV104 - 6915 |  |  |  | Capacitor fails-short. | 15 V power supply will be shorted to ground. On-board electronics will not be powered up. No output available at HV transformer board. | iiSC will be unable to get power from HVT board, but will get power from Universal PSB. Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | On-board fault causing higher current flow. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [11 empty] | 6915
SV104 - 6916 | 24 V Feedback Signal Side Resistor. |  | To provide 24 V sensing feedback path. | Resistor fails-open. | 15 V regulator will keep on working from input side and will not turn off. Which will heat up the resistor on MOSFET Q6 drain and will burn out eventually. No output available at HV transformer board. | iiSC will be unable to get power from HVT board, but will get power from Universal PSB. Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | On-board fault causing higher current flow. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [9 empty] | 0 |  | 6916
SV104 - 6917 |  |  |  | Resistor fails-short. | Over-current will cause the resistor to eventually fail-open. 15 V regulator will keep on working from input side and will not turn off. Which will heat up the resistor on MOSFET Q6 drain and will burn out eventually. No output available at HV transformer board. | iiSC will be unable to get power from HVT board, but will get power from Universal PSB. Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | On-board fault causing higher current flow. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [11 empty] | 6917
SV104 - 6918 | 24 V Feedback Signal Side 9 V Zener Diode. |  | To maintain a constant 9 V drop. | Diode fails-open. | 15 V regulator will keep on working from input side and will not turn off. Which will heat up the resistor on MOSFET Q6 drain and will burn out eventually. No output available at HV transformer board. | iiSC will be unable to get power from HVT board, but will get power from Universal PSB. Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | On-board fault causing higher current flow. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [9 empty] | 0 |  | 6918
SV104 - 6919 |  |  |  | Diode fails-short. | Over-current will cause the diode to eventually fail-open. 15 V regulator will keep on working from input side and will not turn off. Which will heat up the resistor on MOSFET Q6 drain and will burn out eventually. No output available at HV transformer board. | iiSC will be unable to get power from HVT board, but will get power from Universal PSB. Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | On-board fault causing higher current flow. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [11 empty] | 6919
SV104 - 6920 | 24 V Feedback Signal Side MOSFET. |  | To turn OFF power flow controlling MOSFET when auxiliary voltage develops. | MOSFET fails-open. | 15 V regulator will keep on working from input side and will not turn off. Which will heat up the resistor on MOSFET Q6 drain and will burn out eventually. No output available at HV transformer board. | iiSC will be unable to get power from HVT board, but will get power from Universal PSB. Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | On-board fault causing higher current flow. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [11 empty] | 6920
SV104 - 6921 |  |  |  | MOSFET fails-short. | Startup circuitry will remain off permanently as Q6 remains off permanently. 15 V regulator will keep on working from input side and will not turn off. Which will heat up the resistor on MOSFET Q6 drain and will burn out eventually. No output available at HV transformer board. | iiSC will be unable to get power from HVT board, but will get power from Universal PSB. Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | On-board fault causing higher current flow. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [11 empty] | 6921
SV104 - 6922 | 24 V Feedback Signal Side MOSFET.- Zener at Gate |  | To protect MOSFET gate from over-voltage. | Diode fails-open. | Over-voltage protection of MOSFET won't be available. No immediate effect on board in normal operations. | Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Over voltage. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 10 | [9 empty] | 0 |  | 6922
SV104 - 6923 |  |  |  | Diode fails-short. | 15 V regulator will keep on working from input side and will not turn off. Which will heat up the resistor on MOSFET Q6 drain and will burn out eventually. No output available at HV transformer board. | iiSC will be unable to get power from HVT board, but will get power from Universal PSB. Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | On-board fault causing higher current flow. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [11 empty] | 6923
| PWM Controller | [26 empty] | 0
SV104 - 6924 | PWM Controller IC. |  | To provide alternate PWM pulses for full bridge gate driver. | IC output is permanently low. | No PWM will be available for half bridge driver ICs, No output available at HV transformer board. | iiSC will be unable to get power from HVT board, but will get power from Universal PSB. Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | On-board fault causing higher current flow. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [11 empty] | 6924
SV104 - 6925 |  |  |  | One of output is permanently high. | Output of Full Bridge circuit will be 12 V at no load. HV transformer board will have no output as soon as load is applied. | iiSC will be unable to get power from HVT board, but will get power from Universal PSB. Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | On-board fault causing higher current flow. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [11 empty] | 6925
SV104 - 6926 |  |  |  | PWM is having different duty cycle than desired. | Output of Full Bridge circuit will have different duty cycle. HV transformer board will have more or less than 24 V output. | Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | Over voltage. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 2 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 10 | [9 empty] | 0 |  | 6926
SV104 - 6927 | Line Under-Voltage Lockout Voltage Divider High Side Resistor. |  | To turn OFF gate driver PWM in case of under-voltage. | Resistor fails-open. | Under-voltage protection of PWM controller won't be available. No immediate effect on board in normal operations. | Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | Over voltage. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [11 empty] | 6927
SV104 - 6928 |  |  |  | Resistor fails-short. | UVLO pin will get damaged, No PWM will be available for half bridge driver ICs, No output available at HV transformer board. | iiSC will be unable to get power from HVT board, but will get power from Universal PSB. Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | On-board fault causing higher current flow. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [11 empty] | 6928
SV104 - 6929 | Line Under-Voltage Lockout Voltage Divider Low Side Resistor. |  | To turn OFF gate driver PWM in case of under-voltage. | Resistor fails-open. | Under-voltage protection of PWM controller won't be available. No immediate effect on board in normal operations. | Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | Over voltage. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [9 empty] | 0 |  | 6929
SV104 - 6930 |  |  |  | Resistor fails-short. | UVLO pin will get damaged, No PWM will be available for half bridge driver ICs, No output available at HV transformer board. | iiSC will be unable to get power from HVT board, but will get power from Universal PSB. Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | On-board fault causing higher current flow. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [11 empty] | 6930
SV104 - 6931 | RT2 Biasing Resistor. |  | To control oscillator dead time. | Resistor fails-open. | Dead time between alternating PWMs will be altered (maximum). 1 PWM will be permanently high, while other will be permanently low. Output of isolation transformer will not be available. No output available at HV transformer board. | iiSC will be unable to get power from HVT board, but will get power from Universal PSB. Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | On-board fault causing higher current flow. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [9 empty] | 0 |  | 6931
SV104 - 6932 |  |  |  | Resistor fails-short. | Dead time between alternating PWMs will be altered (maximum). 1 PWM will be permanently high, while other will be permanently low. Output of isolation transformer will not be available. No output available at HV transformer board. | iiSC will be unable to get power from HVT board, but will get power from Universal PSB. Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | On-board fault causing higher current flow. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [11 empty] | 6932
SV104 - 6933 | RT1 Biasing Resistor. |  | To control oscillator maximum ON time. | Resistor fails-open. | Dead time between alternating PWMs will be altered (maximum). 1 PWM will be permanently high, while other will be permanently low. Output of isolation transformer will not be available. No output available at HV transformer board. | iiSC will be unable to get power from HVT board, but will get power from Universal PSB. Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | On-board fault causing higher current flow. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [9 empty] | 0 |  | 6933
SV104 - 6934 |  |  |  | Resistor fails-short. | Dead time between alternating PWMs will be altered (maximum). 1 PWM will be permanently high, while other will be permanently low. Output of isolation transformer will not be available. No output available at HV transformer board. | iiSC will be unable to get power from HVT board, but will get power from Universal PSB. Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | On-board fault causing higher current flow. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [11 empty] | 6934
SV104 - 6935 | Restart Timer Resistor. |  | To set PWM restart signal biasing. | Resistor fails-open. | Restart timer functionality will be compromised. No immediate effect on board in normal operations. | Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | Over voltage. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [9 empty] | 0 |  | 6935
SV104 - 6936 |  |  |  | Resistor fails-short. | Restart timer functionality will be compromised. No immediate effect on board in normal operations. | Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | Over voltage. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [11 empty] | 6936
SV104 - 6937 | Soft-Start Capacitor. |  | To provide soft-start biasing value. | Capacitor fails-open. | Soft start functionality will be compromised. No immediate effect on board in normal operations. | Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | Over voltage. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [11 empty] | 6937
SV104 - 6938 |  |  |  | Capacitor fails-short. | Soft start functionality will be compromised. No immediate effect on board in normal operations. | Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | Over voltage. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [11 empty] | 6938
SV104 - 6939 | Ramp Control Resistor. |  | To provide ramp control of PWM. | Resistor fails-open. | PWM ramp will be affected. Output of Full Bridge circuit will be different than desired. HV transformer board will have more or less than 24 V output. | Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | Over voltage. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [9 empty] | 0 |  | 6939
SV104 - 6940 |  |  |  | Resistor fails-short. | PWM ramp will be affected. Output of Full Bridge circuit will be different than desired. HV transformer board will have more or less than 24 V output. | Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | Over voltage. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [11 empty] | 6940
SV104 - 6941 | Current Sense Signal Filtration Capacitor. |  | To filter the CS signal. | Capacitor fails-open. | No immediate effect. | Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | Over voltage. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [9 empty] | 0 |  | 6941
SV104 - 6942 |  |  |  | Capacitor fails-short. | Capacitor will fail-open due to over-current. PWM current limiting functionality will be compromised while the capacitor remains shorted. No immediate effect on board in normal operations. | Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | Over voltage. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [11 empty] | 6942
SV104 - 6943 | Current Sense Capacitor. |  | To limit PWM current. | Capacitor fails-open. | PWM current limiting functionality will be compromised. No immediate effect on board in normal operations. | Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | Over voltage. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [9 empty] | 0 |  | 6943
SV104 - 6944 |  |  |  | Capacitor fails-short. | PWM current limiting functionality will be compromised. No immediate effect on board in normal operations. | Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | Over voltage. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [11 empty] | 6944
SV104 - 6945 | Output Driver Resistor. |  | To limit gate driver current. | Resistor fails-open. | Gate driver PWM path will be broken. No output available at HV transformer board. | iiSC will be unable to get power from HVT board, but will get power from Universal PSB. Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | On-board fault causing higher current flow. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [9 empty] | 0 |  | 6945
SV104 - 6946 |  |  |  | Resistor fails-short. | No immediate till the shorted duration. Resistor will fail-open due to over-current. Gate driver PWM path will be broken. No output available at HV transformer board. | iiSC will be unable to get power from HVT board, but will get power from Universal PSB. Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | On-board fault causing higher current flow. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [11 empty] | 6946
| Full Bridge Circuit | [26 empty] | 0
SV104 - 6947 | Half Bridge Gate Driver IC. |  | To provide gate driver signal for half bridge MOSFETs. | IC output is permanently low. | One half bridge section will not have output. Output of Full Bridge circuit will be 12 V at no load. HV transformer board will have no output as soon as load is applied. | iiSC will be unable to get power from HVT board, but will get power from Universal PSB. Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | On-board fault causing higher current flow. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [11 empty] | 6947
SV104 - 6948 |  |  |  | One of output is permanently high. | One MOSFET will be permanently turned ON. During times, when other MOSFET of same half bridge will turn ON, HV DC line get shorted will ground. Due to high current flow, power MOSFETs may get damaged. Input side fuse will burn out and prevent cascading failures. | iiSC will be unable to get power from HVT board, but will get power from Universal PSB. Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | On-board fault causing higher current flow. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [11 empty] | 6948
SV104 - 6949 |  |  |  | Both outputs are permanently high. | Both MOSFETs will be permanently turned ON. HV DC line will get shorted with ground. Due to high current flow, power MOSFETs may get damaged. Input side fuse will burn out and prevent cascading failures. | iiSC will be unable to get power from HVT board, but will get power from Universal PSB. Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | On-board fault causing higher current flow. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [9 empty] | 0 |  | 6949
SV104 - 6950 | Half Bridge Gate Driver IC - Biasing Capacitor. |  | To provide high side gate driver floating supply. | Capacitor fails-open. | Output of gate driver IC will be affected. No output available at HV transformer board. | iiSC will be unable to get power from HVT board, but will get power from Universal PSB. Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | On-board fault causing higher current flow. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [11 empty] | 6950
SV104 - 6951 |  |  |  | Capacitor fails-short. | Output of gate driver IC will be affected. No output available at HV transformer board. | iiSC will be unable to get power from HVT board, but will get power from Universal PSB. Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | On-board fault causing higher current flow. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [11 empty] | 6951
SV104 - 6952 | Gate Driver Output Circuit - Resistor. |  | To provide path between gate driver IC and gate. | Resistor fails-open. | Output path of gate driver IC will be broken for one MOSFET. Distorted square wave will be available at full bridge circuit output. HV transformer board will have lesser output than desired. | Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | Over voltage. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [11 empty] | 6952
SV104 - 6953 |  |  |  | Resistor fails-short. | Over-current will cause the resistor to eventually fail-open. Output path of gate driver IC will be broken for one MOSFET. Distorted square wave will be available at full bridge circuit output. HV transformer board will have lesser output than desired. | Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | Over voltage. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [11 empty] | 6953
SV104 - 6954 | Gate Driver Output Circuit - General Purpose Diode. |  | To turn off the MOSFET quickly through low resistance path at gate. | Diode fails-open. | MOSFET will turn off through larger resistor which will result in increased switching losses. No immediate effect in case of normal operations. | Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | Over voltage. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [9 empty] | 0 |  | 6954
SV104 - 6955 |  |  |  | Diode fail-short. | Over-current will cause the diode to eventually fail-open. MOSFET will turn off through larger resistor which will result in increased switching losses. No immediate effect in case of normal operations. | Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | Over voltage. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [11 empty] | 6955
SV104 - 6956 | Full Bridge Circuit - MOSFET |  | To convert HV DC to HV AC signal. | MOSFET fails-open. | Distorted square wave will be available at full bridge circuit output. HV transformer board will have lesser output than desired. | Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | Over voltage. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [9 empty] | 0 |  | 6956
SV104 - 6957 |  |  |  | MOSFET fails-short. | No voltage will be available at transformer output, for the shorted duration. No output available at HV transformer board. | iiSC will be unable to get power from HVT board, but will get power from Universal PSB. Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | On-board fault causing higher current flow. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [11 empty] | 6957
SV104 - 6958 | HV Isolation Transformer |  | To step down 400 V AC to 24 V AC. | Primary winding fails-open. | No voltage will be available at transformer output. No output available at HV transformer board. | iiSC will be unable to get power from HVT board, but will get power from Universal PSB. Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | On-board fault causing higher current flow. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [11 empty] | 6958
SV104 - 6959 |  |  |  | Secondary winding fails-open. | High voltage will appear secondary windings of transformer. Small arching may occur. Can cause damage to on-board components. | iiSC will be unable to get power from HVT board, but will get power from Universal PSB. Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | On-board fault causing higher current flow. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [11 empty] | 6959
SV104 - 6960 |  |  |  | Core degradation. | Output voltage will be less than desired value. | Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | Over voltage. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [11 empty] | 6960
SV104 - 6961 |  |  |  | Winding insulation melting. | Turn ratio of transformer will be affected. Output voltage will be less than desired value. | Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | Over voltage. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [11 empty] | 6961
SV104 - 6962 | HV Isolation Transformer - output Side Full Rectifier - Diode |  | To convert 24 V AC to 24 V DC. | Diode fails-open. | Output cut to half if half side is working. | iiSC will be unable to get power from HVT board, but will get power from Universal PSB. Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | On-board fault causing higher current flow. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [9 empty] | 0 |  | 6962
SV104 - 6963 |  |  |  | Diode fails-short. | Secondary winding will get shorted if any diode fails-short. As a result of shortage, excessive amount of current will flow damaging two diodes permanently. Diodes will eventually get open and no output will be available | iiSC will be unable to get power from HVT board, but will get power from Universal PSB. Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | On-board fault causing higher current flow. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [11 empty] | 6963
SV104 - 6964 | HV Isolation Transformer - Feedback Side Full Rectifier - Diode |  | To convert 24 V AC to 24 V DC for feedback. | Diode fails-open. | Output cut to half if half side is working. | iiSC will be unable to get power from HVT board, but will get power from Universal PSB. Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | On-board fault causing higher current flow. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [11 empty] | 6964
SV104 - 6965 |  |  |  | Diode fails-short. | Auxiliary winding will get shorted if any diode fails-short. As a result of shortage, excessive amount of current will flow damaging two diodes permanently. Diodes will eventually get open and no output will be available. | iiSC will be unable to get power from HVT board, but will get power from Universal PSB. Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | On-board fault causing higher current flow. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [9 empty] | 0 |  | 6965
SV104 - 6966 | Output Side Capacitor. |  | To suppress output side ripples and to provide filtration. | Capacitor fails-open. | Output voltage may have ripples. No immediate effect on HV transformer board output. | Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | Over voltage. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [11 empty] | 6966
SV104 - 6967 |  |  |  | Capacitor fails-short. | No voltage available at the output for the shorted duration. | iiSC will be unable to get power from HVT board, but will get power from Universal PSB. Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | On-board fault causing higher current flow. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [11 empty] | 6967
SV104 - 6968 | Heat Sink |  | To provide cooling functionality for power components. | Loose connection between heat sink and power component. | Affected component will face high temperature rise during nominal current operations. Power component may get damaged causing HV transformer board output voltage to drop. | iiSC will be unable to get power from HVT board, but will get power from Universal PSB. Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | On-board fault causing higher current flow. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [11 empty] | 6968
| HV Transformer Board for CLB Driver Board | [26 empty] | 0
| 15 V On-Board Supply | [26 empty] | 0
SV104 - 5528 | Input Side TRIACs. | D13,D12 | Reverse polarity protection. | TRIAC fails-open. | No immediate effect. Parallel TRIAC available for alternate path. | If no other failure is observed on the board, CLB driver board will stay powered. Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | On-board fault causing higher current flow. Excessive forward current. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [11 empty] | 5528
SV104 - 5529 |  |  |  | TRIAC fails-short. | Reverse polarity protection will be compromised during shortage. | If no other failure is observed on the board, CLB driver board will stay powered. Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | Large reverse voltage. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [11 empty] | 5529
SV104 - 6969 |  |  |  | Both TRIACs fail-short. | Reverse polarity protection will be compromised. Board will keep working normally if input is provided with correct polarity. | If no other failure is observed on the board, CLB driver board will stay powered. Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | Large reverse voltage. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [11 empty] | 6969
SV104 - 6970 |  |  |  | Both TRIACs fail-open | Input path will be broken. No output available at HV transformer board. | On Power failure CLB will retain its state. If particular MVAR is in injection and then power failure of its CLB occurs then it will not effect operation and system will remain in injection. If particular MVAR is bypassed its CLB is closed and system is injecting with reduced MVAR and then power failure occurs on closed CLB then system will retain its state and keeps injecting with reduced MVAR. | System will keep working normally. If CLB is stuck in closed state then system will keep injecting with reduced MVAR. . | 2 | On-board fault causing higher current flow. Excessive forward current. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | Failure will be detected by firmware by verifying the CARD_HEALTHY feedback (High when power fails). | 2 | 4 | CLB03? | CLB Card Unhealthy | [9 empty] | 6970
SV104-11017 |  |  |  | Both TRIACs fail-open and then fault occurs that engages CLB | Input path will be broken. No output available at HV transformer board. | If CLB is open, power failure occur and system is in injection and due to iiSC fault now faulty MVAR cannot be bypassed so system will transit to monitoring mode. System cannot go to injection anymore until the fault is cleared. | System will lose injection capability until the MVAR fault is cleared. | 4 | On-board fault causing higher current flow. Excessive forward current. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 4 | HALT. Electrical Stress Testing. Thermal Stress Testing. | Failure will be detected by firmware by verifying the CARD_HEALTHY feedback (High when power fails). | 2 | 8 | CLB03? | CLB Card Unhealthy | [9 empty] | 11017
SV104 - 5530 | Input Side Fuse. | F2 | To cut-off supply in case of over-current. | Fuse fails-open. | Input power path will be broken. No output available at HV transformer board. | On Power failure CLB will retain its state. If particular MVAR is in injection and then power failure of its CLB occurs then it will not effect operation and system will remain in injection. If particular MVAR is bypassed its CLB is closed and system is injecting with reduced MVAR and then power failure occurs on closed CLB then system will retain its state and keeps injecting with reduced MVAR. | System will keep working normally. If CLB is stuck in closed state then system will keep injecting with reduced MVAR. . | 2 | Degradation of components. Bad component batch. Overcurrent. | Usage of over-rated components. Conformal coating. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | Failure will be detected by firmware by verifying the CARD_HEALTHY feedback (High when power fails). | 2 | 4 | CLB03? | CLB Card Unhealthy | [9 empty] | 5530
SV104-11018 |  |  |  | Fuse fails-open and then fault occurs that engages CLB | Input power path will be broken. No output available at HV transformer board. | If CLB is open, power failure occur and system is in injection and due to iiSC fault now faulty MVAR cannot be bypassed so system will transit to monitoring mode. System cannot go to injection anymore until the fault is cleared. | System will lose injection capability until the MVAR fault is cleared. | 4 | Degradation of components. Bad component batch. Overcurrent. | Usage of over-rated components. Conformal coating. | 1 | 4 | HALT. Electrical Stress Testing. Thermal Stress Testing. | Failure will be detected by firmware by verifying the CARD_HEALTHY feedback (High when power fails). | 2 | 8 | CLB03? | CLB Card Unhealthy | [9 empty] | 11018
SV104 - 5531 | Input Side Filter Capacitors. | C2,C23 | To suppress ripples on input voltage. | Capacitor fails-open. | No immediate effect due to presence of redundant capacitor as well as input supply is regulated supply. | If no other failure is observed on the board, CLB driver board will stay powered. Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | Mechanical stress. Localized heating for long time will separate end connection of capacitor. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [11 empty] | 5531
SV104 - 5532 |  |  |  | Capacitor fails-short. | PHT-DC Capacitor will dump full energy in HV-ISO board leaving it permanently damage (Trace damage). No output available at HV transformer board. | On Power failure CLB will retain its state. If particular MVAR is in injection and then power failure of its CLB occurs then it will not effect operation and system will remain in injection. If particular MVAR is bypassed its CLB is closed and system is injecting with reduced MVAR and then power failure occurs on closed CLB then system will retain its state and keeps injecting with reduced MVAR. | System will keep working normally. If CLB is stuck in closed state then system will keep injecting with reduced MVAR. . | 2 | Over voltage. De-gradation of components. Water ingress during humidity condition as it is film capacitor. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. RTV application on edges to stop water ingress. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. Environmental Testing. | Failure will be detected by firmware by verifying the CARD_HEALTHY feedback (High when power fails). | 2 | 4 | CLB03? | CLB Card Unhealthy | [9 empty] | 5532
SV104-11019 |  |  |  | Capacitor fails-short and then fault occurs that engages CLB. | PHT-DC Capacitor will dump full energy in HV-ISO board leaving it permanently damage (Trace damage). No output available at HV transformer board. | If CLB is open, power failure occur and system is either in monitoring or injection and due to iiSC fault now faulty MVAR cannot be bypassed so system will transit to monitoring mode if injection is going on. System cannot go to injection anymore until the fault is cleared. | System will lose injection capability until the MVAR fault is cleared. | 4 | Over voltage. De-gradation of components. Water ingress during humidity condition as it is film capacitor. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. RTV application on edges to stop water ingress. | 1 | 4 | HALT. Electrical Stress Testing. Thermal Stress Testing. Environmental Testing. | Failure will be detected by firmware by verifying the CARD_HEALTHY feedback (High when power fails). | 2 | 8 | CLB03? | CLB Card Unhealthy | [9 empty] | 11019
SV104 - 5533 | Low Voltage Detection Zener Diode. (D7, D11, D10) | D7,D10,D11 | To set under-voltage lockout threshold. | Diode fails-open. | No voltage will be available at power controlling MOSFET gate. On-board 15 V supply will not be available. No output available at HV transformer board. | On Power failure CLB will retain its state. If particular MVAR is in injection and then power failure of its CLB occurs then it will not effect operation and system will remain in injection. If particular MVAR is bypassed its CLB is closed and system is injecting with reduced MVAR and then power failure occurs on closed CLB then system will retain its state and keeps injecting with reduced MVAR. | System will keep working normally. If CLB is stuck in closed state then system will keep injecting with reduced MVAR. . | 2 | Degradation of components. Overcurrent. Bad component batch. Mechanical stress or damage during assembly. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 2 | 4 | HALT. Electrical Stress Testing. Thermal Stress Testing. | Failure will be detected by firmware by verifying the CARD_HEALTHY feedback (High when power fails). | 2 | 8 | CLB03? | CLB Card Unhealthy | [9 empty] | 5533
SV104-11020 |  |  |  | Diode fails-open and then fault occurs that engages CLB. | No voltage will be available at power controlling MOSFET gate. On-board 15 V supply will not be available. No output available at HV transformer board. | If CLB is open, power failure occur and system is either in monitoring or injection and due to iiSC fault now faulty MVAR cannot be bypassed so system will transit to monitoring mode if injection is going on. System cannot go to injection anymore until the fault is cleared. | System will lose injection capability until the MVAR fault is cleared. | 4 | Degradation of components. Overcurrent. Bad component batch. Mechanical stress or damage during assembly. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 2 | 4 | HALT. Electrical Stress Testing. Thermal Stress Testing. | Failure will be detected by firmware by verifying the CARD_HEALTHY feedback (High when power fails). | 2 | 16 | CLB03? | CLB Card Unhealthy | [9 empty] | 11020
SV104 - 5534 |  |  |  | Diode fails-short.. | The threshold for UVLO detection will decrease. Board will turn on before the set threshold of 320 V. Slight effect will be on PHT-DC bus during low line current condition as it will ramp up slowly. Board will keep working. | If no other failure is observed on the board, CLB driver board will stay powered. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Degradation of components. Overvoltage. Bad component batch. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 2 | 4 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 20 | [11 empty] | 5534
SV104-11021 | Low Voltage Detection Voltage Divider | R41,R36 | To set UVLO threshold | Resistor fails-open. | No voltage will be available at power controlling MOSFET gate. On-board 15 V supply will not be available. No output available at HV transformer board. | On Power failure CLB will retain its state. If particular MVAR is in injection and then power failure of its CLB occurs then it will not effect operation and system will remain in injection. If particular MVAR is bypassed its CLB is closed and system is injecting with reduced MVAR and then power failure occurs on closed CLB then system will retain its state and keeps injecting with reduced MVAR. | System will keep working normally. If CLB is stuck in closed state then system will keep injecting with reduced MVAR. . | 2 | Over voltage. Over Temperature. Over stress due to shock or vibration. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. Vibration testing. | None. | 5 | 10 | [11 empty] | 11021
SV104-11022 |  |  |  | Resistor fails-open and then fault occurs that engages CLB. | No voltage will be available at power controlling MOSFET gate. On-board 15 V supply will not be available. No output available at HV transformer board. | If CLB is open, power failure occur and system is either in monitoring or injection and due to iiSC fault now faulty MVAR cannot be bypassed so system will transit to monitoring mode if injection is going on. System cannot go to injection anymore until the fault is cleared. | System will lose injection capability until the MVAR fault is cleared. | 4 | Over voltage. Over Temperature. Over stress due to shock or vibration. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 4 | HALT. Electrical Stress Testing. Thermal Stress Testing. Vibration testing. | Failure will be detected by firmware by verifying the CARD_HEALTHY feedback (High when power fails). | 2 | 8 | CLB03? | CLB Card Unhealthy | [9 empty] | 11022
SV104-11023 |  |  |  | Resistor fails-short. | UVLO limit will decrease. Board will powerup at lower voltage. Board will keep working. | If no other failure is observed on the board, CLB driver board will stay powered. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Wear-out due to extensive use. Excessive humidity. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. Vibration testing. | None. | 5 | 10 | [9 empty] | 0 |  | 11023
SV104 - 5535 | Input Side current limiting Resistor. | R30,R31,R32,R33,R34,R35 | To control input current. | Resistor fails-open. | No voltage will be available at power controlling MOSFET gate. On-board 15 V supply will not be available. No output available at HV transformer board. | On Power failure CLB will retain its state. If particular MVAR is in injection and then power failure of its CLB occurs then it will not effect operation and system will remain in injection. If particular MVAR is bypassed its CLB is closed and system is injecting with reduced MVAR and then power failure occurs on closed CLB then system will retain its state and keeps injecting with reduced MVAR. | System will keep working normally. If CLB is stuck in closed state then system will keep injecting with reduced MVAR. . | 2 | Degradation of components. Overcurrent. Counterfeit part. Overstress due to shock or vibration. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. Vibration testing. | Failure will be detected by firmware by verifying the CARD_HEALTHY feedback (High when power fails). | 2 | 4 | CLB03? | CLB Card Unhealthy | [7 empty] | 0 |  | 5535
SV104-11024 |  |  |  | Resistor fails-open and then fault occurs that engages CLB. | No voltage will be available at power controlling MOSFET gate. On-board 15 V supply will not be available. No output available at HV transformer board. | If CLB is open, power failure occur and system is either in monitoring or injection and due to iiSC fault now faulty MVAR cannot be bypassed so system will transit to monitoring mode if injection is going on. System cannot go to injection anymore until the fault is cleared. | System will lose injection capability until the MVAR fault is cleared. | 4 | Degradation of components. Overcurrent. Counterfeit part. Overstress due to shock or vibration. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 4 | HALT. Electrical Stress Testing. Thermal Stress Testing. Vibration testing. | Failure will be detected by firmware by verifying the CARD_HEALTHY feedback (High when power fails). | 2 | 8 | CLB03? | CLB Card Unhealthy | [7 empty] | 0 |  | 11024
SV104 - 5536 |  |  |  | Any one resistor fails-short. | No immediate effect on board. Board will keep working normally. | If no other failure is observed on the board, CLB driver board will stay powered. Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | Degradation of components. Counterfeit part. High humidity. | Usage of over-rated components. Using components with industrial grade scale. Conformal coating. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. Environmental testing. | None. | 5 | 5 | [11 empty] | 5536
SV104-12397 |  |  |  | More than one resistors fails-short. | Soft starting current is increased significantly consequently MOSFET power dissipation will increase that could bring failure. No output available at HV transformer board. | On Power failure CLB will retain its state. If particular MVAR is in injection and then power failure of its CLB occurs then it will not effect operation and system will remain in injection. If particular MVAR is bypassed its CLB is closed and system is injecting with reduced MVAR and then power failure occurs on closed CLB then system will retain its state and keeps injecting with reduced MVAR. | System will keep working normally. If CLB is stuck in closed state then system will keep injecting with reduced MVAR. . | 2 | Wear-out due to extensive use. Excessive humidity. Counterfeit part. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements.. Conformal coating. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. Vibration testing. | Failure will be detected by firmware by verifying the CARD_HEALTHY feedback (High when power fails). | 2 | 4 | CLB03? | CLB Card Unhealthy | [9 empty] | 12397
SV104-12398 |  |  |  | More than one resistors fails-short and then fault occurs that engages CLB. | Soft starting current is increased significantly consequently MOSFET power dissipation will increase that could bring failure. No output available at HV transformer board. | If CLB is open, power failure occur and system is either in monitoring or injection and due to iiSC fault now faulty MVAR cannot be bypassed so system will transit to monitoring mode if injection is going on. System cannot go to injection anymore until the fault is cleared. | System will lose injection capability until the MVAR fault is cleared. | 4 | Wear-out due to extensive use. Excessive humidity. Counterfeit part. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements.. Conformal coating. | 1 | 4 | HALT. Electrical Stress Testing. Thermal Stress Testing. Vibration testing. | Failure will be detected by firmware by verifying the CARD_HEALTHY feedback (High when power fails). | 2 | 8 | CLB03? | CLB Card Unhealthy | [9 empty] | 12398
SV104 - 5537 | Input Power Control MOSFET. | Q6 | To turn ON/OFF power flow. | MOSFET fails-open. | Input power path will be broken. No output available at HV transformer board. | On Power failure CLB will retain its state. If particular MVAR is in injection and then power failure of its CLB occurs then it will not effect operation and system will remain in injection. If particular MVAR is bypassed its CLB is closed and system is injecting with reduced MVAR and then power failure occurs on closed CLB then system will retain its state and keeps injecting with reduced MVAR. | System will keep working normally. If CLB is stuck in closed state then system will keep injecting with reduced MVAR. . | 2 | Overheating Mechanical stress resulting in cracked MOSFET body. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | Failure will be detected by firmware by verifying the CARD_HEALTHY feedback (High when power fails). | 2 | 4 | CLB03? | CLB Card Unhealthy | [9 empty] | 5537
SV104-11025 |  |  |  | MOSFET fails-open and then fault occurs that engages CLB. | Input power path will be broken. No output available at HV transformer board. | If CLB is open, power failure occur and system is either in monitoring or injection and due to iiSC fault now faulty MVAR cannot be bypassed so system will transit to monitoring mode if injection is going on. System cannot go to injection anymore until the fault is cleared. | System will lose injection capability until the MVAR fault is cleared. | 4 | Overheating Mechanical stress resulting in cracked MOSFET body. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 4 | HALT. Electrical Stress Testing. Thermal Stress Testing. | Failure will be detected by firmware by verifying the CARD_HEALTHY feedback (High when power fails). | 2 | 8 | CLB03? | CLB Card Unhealthy | [7 empty] | 0 |  | 11025
SV104 - 5538 |  |  |  | MOSFET fails-short. | Startup circuitry will turn on permanently resulting in overheating and permanently damage to startup resistor. No output available once HV-ISO reboot. | On Power failure CLB will retain its state. If particular MVAR is in injection and then power failure of its CLB occurs then it will not effect operation and system will remain in injection. If particular MVAR is bypassed its CLB is closed and system is injecting with reduced MVAR and then power failure occurs on closed CLB then system will retain its state and keeps injecting with reduced MVAR. | System will keep working normally. If CLB is stuck in closed state then system will keep injecting with reduced MVAR. . | 2 | Transients Overheating as a result of loose connection with heat sink Overcurrent Counterfeit part Damage during mechanical assembly of board Metallic debris stuck in between terminals | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Conformal coating. | 2 | 4 | HALT. Electrical Stress Testing. Thermal Stress Testing. | Failure will be detected by firmware by verifying the CARD_HEALTHY feedback (High when power fails). | 2 | 8 | CLB03? | CLB Card Unhealthy | [9 empty] | 5538
SV104-11026 |  |  |  | MOSFET fails-short and then fault occurs that engages CLB. | Startup circuitry will turn on permanently resulting in overheating and permanently damage to startup resistor. No output available once HV-ISO reboot. | If CLB is open, power failure occur and system is either in monitoring or injection and due to iiSC fault now faulty MVAR cannot be bypassed so system will transit to monitoring mode if injection is going on. System cannot go to injection anymore until the fault is cleared. | System will lose injection capability until the MVAR fault is cleared. | 4 | Transients Overheating as a result of loose connection with heat sink Overcurrent Counterfeit part Damage during mechanical assembly of board Metallic debris stuck in between terminals | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Conformal coating. | 1 | 4 | HALT. Electrical Stress Testing. Thermal Stress Testing. | Failure will be detected by firmware by verifying the CARD_HEALTHY feedback (High when power fails). | 2 | 8 | CLB03? | CLB Card Unhealthy | [9 empty] | 11026
SV104 - 5539 | Over-voltage Protection Zener Diode at MOSFET Gate Side. | D31 | For gate protection of MOSFET. | Diode fails-open. | Over-voltage protection of MOSFET won't be available. No immediate effect on board in normal operations. | If no other failure is observed on the board, CLB driver board will stay powered. Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | Degradation of components. Overcurrent. Bad component batch. Mechanical stress or damage during assembly. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 2 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 10 | [11 empty] | 5539
SV104 - 5540 |  |  |  | Diode fails-short. | MOSFET will be turned off completely. Startup circuit will not work. No output available at HV transformer board. | On Power failure CLB will retain its state. If particular MVAR is in injection and then power failure of its CLB occurs then it will not effect operation and system will remain in injection. If particular MVAR is bypassed its CLB is closed and system is injecting with reduced MVAR and then power failure occurs on closed CLB then system will retain its state and keeps injecting with reduced MVAR. | System will keep working normally. If CLB is stuck in closed state then system will keep injecting with reduced MVAR. . | 2 | Degradation of components. Overvoltage. Counterfeit part. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 2 | 4 | HALT. Electrical Stress Testing. Thermal Stress Testing. | Failure will be detected by firmware by verifying the CARD_HEALTHY feedback (High when power fails). | 2 | 8 | CLB03? | CLB Card Unhealthy | [7 empty] | 0 |  | 5540
SV104-11027 |  |  |  | Diode fails-short and then fault occurs that engages CLB. | MOSFET will be turned off completely. Startup circuit will not work. No output available at HV transformer board. | If CLB is open, power failure occur and system is in injection and due to iiSC fault now faulty MVAR cannot be bypassed so system will transit to monitoring mode. System cannot go to injection anymore until the fault is cleared. | System will lose injection capability until the MVAR fault is cleared. | 4 | Degradation of components. Overvoltage. Counterfeit part. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 4 | HALT. Electrical Stress Testing. Thermal Stress Testing. | Failure will be detected by firmware by verifying the CARD_HEALTHY feedback (High when power fails). | 2 | 8 | CLB03? | CLB Card Unhealthy | [9 empty] | 11027
SV104-12399 | Filtration Capacitor | C21 | To suppress noise and remove ripples | Capacitor fails-open. | No immediate effect on board. Board will keep working normally. | If no other failure is observed on the board, CLB driver board will stay powered. Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | Mechanical stress. Localized heating for long time will separate end connection of capacitor. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. Vibration Testing. | None. | 5 | 5 | [11 empty] | 12399
SV104-12400 |  |  |  | Capacitor fails-short. | HVDC and 24VAUX will be shorted top ground. Startup circuit will not work. Input Fuse Will be Blown No output available at HV transformer board. | On Power failure CLB will retain its state. If particular MVAR is in injection and then power failure of its CLB occurs then it will not effect operation and system will remain in injection. If particular MVAR is bypassed its CLB is closed and system is injecting with reduced MVAR and then power failure occurs on closed CLB then system will retain its state and keeps injecting with reduced MVAR. | System will keep working normally. If CLB is stuck in closed state then system will keep injecting with reduced MVAR. . | 2 | Wear-out due to dielectric degradation. High-voltage transients. De-gradation of components. Water ingress during humidity condition as it is film capacitor. Overvoltage | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. RTV application on edges to stop water ingress. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. Environmental Testing. | Failure will be detected by firmware by verifying the CARD_HEALTHY feedback (High when power fails). | 2 | 4 | CLB03? | CLB Card Unhealthy | [9 empty] | 12400
SV104-12401 |  |  |  | Capacitor fails-short and then fault occurs that engages CLB. | HVDC and 24VAUX will be shorted top ground. Startup circuit will not work. Input Fuse Will be Blown No output available at HV transformer board. | If CLB is open, power failure occur and system is in injection and due to iiSC fault now faulty MVAR cannot be bypassed so system will transit to monitoring mode. System cannot go to injection anymore until the fault is cleared. | System will lose injection capability until the MVAR fault is cleared. | 4 | Wear-out due to dielectric degradation. High-voltage transients. De-gradation of components. Water ingress during humidity condition as it is film capacitor. Overvoltage | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. RTV application on edges to stop water ingress. | 1 | 4 | HALT. Electrical Stress Testing. Thermal Stress Testing. | Failure will be detected by firmware by verifying the CARD_HEALTHY feedback (High when power fails). | 2 | 8 | CLB03? | CLB Card Unhealthy | [9 empty] | 12401
SV104-11028 | MOSFET resistance for Miller Capacitance | R37 | To discharge miller capacitance of MOSFET | Resistor fails-open | Abnormal Behavior of MOSFET Might turn ON/OFF abnormally. Once Board Reboots no output will be available No output available at HV transformer board | On Power failure CLB will retain its state. If particular MVAR is in injection and then power failure of its CLB occurs then it will not effect operation and system will remain in injection. If particular MVAR is bypassed its CLB is closed and system is injecting with reduced MVAR and then power failure occurs on closed CLB then system will retain its state and keeps injecting with reduced MVAR. | System will keep working normally. If CLB is stuck in closed state then system will keep injecting with reduced MVAR. . | 2 | Over voltage. Over Temperature. Over stress due to shock or vibration. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. Vibration testing. | Failure will be detected by firmware by verifying the CARD_HEALTHY feedback (High when power fails). | 2 | 4 | CLB03? | CLB Card Unhealthy | [9 empty] | 11028
SV104-11029 |  |  |  | Resistor fails-open and then fault occurs that engages CLB. | Abnormal Behavior of MOSFET Might turn ON/OFF abnormally. Once Board Reboots no output will be available No output available at HV transformer board | If CLB is open, power failure occur and system is in injection and due to iiSC fault now faulty MVAR cannot be bypassed so system will transit to monitoring mode. System cannot go to injection anymore until the fault is cleared. | System will lose injection capability until the MVAR fault is cleared. | 4 | Over voltage. Over Temperature. Over stress due to shock or vibration. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 4 | HALT. Electrical Stress Testing. Thermal Stress Testing. Vibration testing. | Failure will be detected by firmware by verifying the CARD_HEALTHY feedback (High when power fails). | 2 | 8 | CLB03? | CLB Card Unhealthy | [7 empty] | 0 |  | 11029
SV104-11030 |  |  |  | Resistor fails-short | Gate and Source of Q6 will have no voltage difference so MOSFET cannot operate No output available at HV transformer board | If CLB is open, power failure occur and system is either in monitoring or injection and due to iiSC fault now faulty MVAR cannot be bypassed so system will transit to monitoring mode if injection is going on. System cannot go to injection anymore until the fault is cleared. | System will lose injection capability until the MVAR fault is cleared. | 2 | Wear-out due to extensive use. Excessive humidity. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. Vibration testing. | Failure will be detected by firmware by verifying the CARD_HEALTHY feedback (High when power fails). | 2 | 4 | CLB03? | CLB Card Unhealthy | [9 empty] | 11030
SV104 - 6971 | D21-Free wheeling diode | D21 | To protect BJT during reverse voltage condition | Diode fails-open. | No protection for BJT will be available. Reverse voltage development across BJT will damage it. No output available. | On Power failure CLB will retain its state. If particular MVAR is in injection and then power failure of its CLB occurs then it will not effect operation and system will remain in injection. If particular MVAR is bypassed its CLB is closed and system is injecting with reduced MVAR and then power failure occurs on closed CLB then system will retain its state and keeps injecting with reduced MVAR. | System will keep working normally. If CLB is stuck in closed state then system will keep injecting with reduced MVAR. . | 2 | On-board fault causing higher current flow. Excessive forward current. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | Failure will be detected by firmware by verifying the CARD_HEALTHY feedback (High when power fails). | 2 | 4 | CLB03? | CLB Card Unhealthy | [7 empty] | 0 |  | 6971
SV104-11031 |  |  |  | Diode fails-open and then fault occurs that engages CLB. | No protection for BJT will be available. Reverse voltage development across BJT will damage it. No output available. | If CLB is open, power failure occur and system is in injection and due to iiSC fault now faulty MVAR cannot be bypassed so system will transit to monitoring mode. System cannot go to injection anymore until the fault is cleared. | System will lose injection capability until the MVAR fault is cleared. | 4 | On-board fault causing higher current flow. Excessive forward current. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 4 | HALT. Electrical Stress Testing. Thermal Stress Testing. | Failure will be detected by firmware by verifying the CARD_HEALTHY feedback (High when power fails). | 2 | 8 | CLB03? | CLB Card Unhealthy | [9 empty] | 11031
SV104 - 6972 |  |  |  | Diode fails-short. | Input will appear as it is on output which will damage PWM controller and gate driver ICs permanently. No output available. | On Power failure CLB will retain its state. If particular MVAR is in injection and then power failure of its CLB occurs then it will not effect operation and system will remain in injection. If particular MVAR is bypassed its CLB is closed and system is injecting with reduced MVAR and then power failure occurs on closed CLB then system will retain its state and keeps injecting with reduced MVAR. | System will keep working normally. If CLB is stuck in closed state then system will keep injecting with reduced MVAR. . | 2 | Large reverse voltage. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | Failure will be detected by firmware by verifying the CARD_HEALTHY feedback (High when power fails). | 2 | 4 | CLB03? | CLB Card Unhealthy | [9 empty] | 6972
SV104-11032 |  |  |  | Diode fails-short and then fault occurs that engages CLB. | Input will appear as it is on output which will damage PWM controller and gate driver ICs permanently. No output available. | If CLB is open, power failure occur and system is in injection and due to iiSC fault now faulty MVAR cannot be bypassed so system will transit to monitoring mode. System cannot go to injection anymore until the fault is cleared. | System will lose injection capability until the MVAR fault is cleared. | 4 | On-board fault causing higher current flow. Excessive forward current. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 4 | HALT. Electrical Stress Testing. Thermal Stress Testing. | Failure will be detected by firmware by verifying the CARD_HEALTHY feedback (High when power fails). | 2 | 8 | CLB03? | CLB Card Unhealthy | [7 empty] | 0 |  | 11032
SV104 - 6973 | D22-To prevent reverse power flow | D22 | To prevent reverse power flow from auxiliary to startup circuitry | Diode fails-open. | Input power path will be broken. No output available at HV transformer board. | On Power failure CLB will retain its state. If particular MVAR is in injection and then power failure of its CLB occurs then it will not effect operation and system will remain in injection. If particular MVAR is bypassed its CLB is closed and system is injecting with reduced MVAR and then power failure occurs on closed CLB then system will retain its state and keeps injecting with reduced MVAR. | System will keep working normally. If CLB is stuck in closed state then system will keep injecting with reduced MVAR. . | 2 | On-board fault causing higher current flow. Excessive forward current. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | Failure will be detected by firmware by verifying the CARD_HEALTHY feedback (High when power fails). | 2 | 4 | CLB03? | CLB Card Unhealthy | [9 empty] | 6973
SV104-11033 |  |  |  | Diode fails-open and than Fault occurs that engages CLB. | Input power path will be broken. No output available at HV transformer board. | If CLB is open, power failure occur and system is in injection and due to iiSC fault now faulty MVAR cannot be bypassed so system will transit to monitoring mode. System cannot go to injection anymore until the fault is cleared. | System will lose injection capability until the MVAR fault is cleared. | 4 | On-board fault causing higher current flow. Excessive forward current. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 4 | HALT. Electrical Stress Testing. Thermal Stress Testing. | Failure will be detected by firmware by verifying the CARD_HEALTHY feedback (High when power fails). | 2 | 8 | CLB03? | CLB Card Unhealthy | [9 empty] | 11033
SV104 - 6974 |  |  |  | Diode fails-short. | If the board is OFF than it can not turn ON. If board is ON than reverse power will start to flow. D31 will be forward biased and as gate of Q6 is grounded than 24VAUX will also be grounded. No output available at HV transformer board. | On Power failure CLB will retain its state. If particular MVAR is in injection and then power failure of its CLB occurs then it will not effect operation and system will remain in injection. If particular MVAR is bypassed its CLB is closed and system is injecting with reduced MVAR and then power failure occurs on closed CLB then system will retain its state and keeps injecting with reduced MVAR. | System will keep working normally. If CLB is stuck in closed state then system will keep injecting with reduced MVAR. . | 2 | Large reverse voltage. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 10 | CLB03? | CLB Card Unhealthy | [9 empty] | 6974
SV104-12402 |  |  |  | Diode fails-short and than Fault occurs that engages CLB. | If the board is OFF than it can not turn ON. If board is ON than reverse power will start to flow. D31 will be forward biased and as gate of Q6 is grounded than 24VAUX will also be grounded. No output available at HV transformer board. | If CLB is open, power failure occur and system is in injection and due to iiSC fault now faulty MVAR cannot be bypassed so system will transit to monitoring mode. System cannot go to injection anymore until the fault is cleared. | System will lose injection capability until the MVAR fault is cleared. | 4 | Large reverse voltage. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 4 | HALT. Electrical Stress Testing. Thermal Stress Testing. | Failure will be detected by firmware by verifying the CARD_HEALTHY feedback (High when power fails). | 2 | 8 | CLB03? | CLB Card Unhealthy | [9 empty] | 12402
SV104 - 6975 | D27-Zener diode | D27 | To set reference voltage for BJT to regulate | Diode fails-open. | Voltage at input will appear as it is on output damaging controller and regulator permanently. No output available at HV transformer board. | On Power failure CLB will retain its state. If particular MVAR is in injection and then power failure of its CLB occurs then it will not effect operation and system will remain in injection. If particular MVAR is bypassed its CLB is closed and system is injecting with reduced MVAR and then power failure occurs on closed CLB then system will retain its state and keeps injecting with reduced MVAR. | System will keep working normally. If CLB is stuck in closed state then system will keep injecting with reduced MVAR. . | 2 | On-board fault causing higher current flow. Excessive forward current. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 2 | 4 | HALT. Electrical Stress Testing. Thermal Stress Testing. | Failure will be detected by firmware by verifying the CARD_HEALTHY feedback (High when power fails). | 2 | 8 | CLB03? | CLB Card Unhealthy | [9 empty] | 6975
SV104-11034 |  |  |  | Diode fails-open and than Fault occurs that engages CLB. | Voltage at input will appear as it is on output damaging controller and regulator permanently. No output available at HV transformer board. | If CLB is open, power failure occur and system is in injection and due to iiSC fault now faulty MVAR cannot be bypassed so system will transit to monitoring mode. System cannot go to injection anymore until the fault is cleared. | System will lose injection capability until the MVAR fault is cleared. | 4 | On-board fault causing higher current flow. Excessive forward current. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 2 | 8 | HALT. Electrical Stress Testing. Thermal Stress Testing. | Failure will be detected by firmware by verifying the CARD_HEALTHY feedback (High when power fails). | 2 | 16 | CLB03? | CLB Card Unhealthy | [9 empty] | 11034
SV104 - 6976 |  |  |  | Diode fails-short. | BJT will not turn on. No output available at HV transformer board. | On Power failure CLB will retain its state. If particular MVAR is in injection and then power failure of its CLB occurs then it will not effect operation and system will remain in injection. If particular MVAR is bypassed its CLB is closed and system is injecting with reduced MVAR and then power failure occurs on closed CLB then system will retain its state and keeps injecting with reduced MVAR. | System will keep working normally. If CLB is stuck in closed state then system will keep injecting with reduced MVAR. . | 2 | Large reverse voltage. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 2 | 4 | HALT. Electrical Stress Testing. Thermal Stress Testing. | Failure will be detected by firmware by verifying the CARD_HEALTHY feedback (High when power fails). | 2 | 8 | CLB03? | CLB Card Unhealthy | [9 empty] | 6976
SV104-11035 |  |  |  | Diode fails-short and than Fault occurs that engages CLB. | BJT will not turn on. No output available at HV transformer board. | If CLB is open, power failure occur and system is in injection and due to iiSC fault now faulty MVAR cannot be bypassed so system will transit to monitoring mode. System cannot go to injection anymore until the fault is cleared. | System will lose injection capability until the MVAR fault is cleared. | 4 | Large reverse voltage. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 2 | 8 | HALT. Electrical Stress Testing. Thermal Stress Testing. | Failure will be detected by firmware by verifying the CARD_HEALTHY feedback (High when power fails). | 2 | 16 | CLB03? | CLB Card Unhealthy | [9 empty] | 11035
SV104 - 5541 | Input Power Control BJT. | Q8 | To provide regulated voltage for startup. | BJT fails-open. | Input power path will be broken. No output available at HV transformer board. | On Power failure CLB will retain its state. If particular MVAR is in injection and then power failure of its CLB occurs then it will not effect operation and system will remain in injection. If particular MVAR is bypassed its CLB is closed and system is injecting with reduced MVAR and then power failure occurs on closed CLB then system will retain its state and keeps injecting with reduced MVAR. | System will keep working normally. If CLB is stuck in closed state then system will keep injecting with reduced MVAR. . | 2 | Melted connections due to overheating. Manufacturing defect. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | Failure will be detected by firmware by verifying the CARD_HEALTHY feedback (High when power fails). | 2 | 4 | CLB03? | CLB Card Unhealthy | [9 empty] | 5541
SV104-11036 |  |  |  | BJT fails-open and than fault occurs that engages CLB | Input power path will be broken. No output available at HV transformer board. | If CLB is open, power failure occur and system is in injection and due to iiSC fault now faulty MVAR cannot be bypassed so system will transit to monitoring mode. System cannot go to injection anymore until the fault is cleared. | System will lose injection capability until the MVAR fault is cleared. | 4 | Melted connections due to overheating. Manufacturing defect. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 4 | HALT. Electrical Stress Testing. Thermal Stress Testing. | Failure will be detected by firmware by verifying the CARD_HEALTHY feedback (High when power fails). | 2 | 8 | CLB03? | CLB Card Unhealthy | [9 empty] | 11036
SV104 - 5542 |  |  |  | BJT fails-short. | Higher voltage at startup will damage the PWM controller and gate drivers of board. Input power path will be broken. No output available at HV transformer board. | On Power failure CLB will retain its state. If particular MVAR is in injection and then power failure of its CLB occurs then it will not effect operation and system will remain in injection. If particular MVAR is bypassed its CLB is closed and system is injecting with reduced MVAR and then power failure occurs on closed CLB then system will retain its state and keeps injecting with reduced MVAR. | System will keep working normally. If CLB is stuck in closed state then system will keep injecting with reduced MVAR. . | 2 | Over voltage. Leakage at junctions. Wear-out due to high power dissipation. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | Failure will be detected by firmware by verifying the CARD_HEALTHY feedback (High when power fails). | 2 | 4 | CLB03? | CLB Card Unhealthy | [9 empty] | 5542
SV104-11037 |  |  |  | BJT fails-short and than fault occurs that engages CLB | Higher voltage at startup will damage the PWM controller and gate drivers of board. Input power path will be broken. No output available at HV transformer board. | If CLB is open, power failure occur and system is in injection and due to iiSC fault now faulty MVAR cannot be bypassed so system will transit to monitoring mode. System cannot go to injection anymore until the fault is cleared. | System will lose injection capability until the MVAR fault is cleared. | 4 | On-board fault causing higher current flow. Excessive forward current. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 4 | HALT. Electrical Stress Testing. Thermal Stress Testing. | Failure will be detected by firmware by verifying the CARD_HEALTHY feedback (High when power fails). | 2 | 8 | CLB03? | CLB Card Unhealthy | [9 empty] | 11037
SV104 - 5543 | Biasing Resistor for BJT. | R40 | To set biasing threshold for power flow controlling BJT. | Resistor fails-open. | BJT will be permanently turned OFF. Input power path will be broken. No output available at HV transformer board. | On Power failure CLB will retain its state. If particular MVAR is in injection and then power failure of its CLB occurs then it will not effect operation and system will remain in injection. If particular MVAR is bypassed its CLB is closed and system is injecting with reduced MVAR and then power failure occurs on closed CLB then system will retain its state and keeps injecting with reduced MVAR. | System will keep working normally. If CLB is stuck in closed state then system will keep injecting with reduced MVAR. . | 2 | Over voltage. Over Temperature. Over stress due to shock or vibration. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | Failure will be detected by firmware by verifying the CARD_HEALTHY feedback (High when power fails). | 2 | 4 | CLB03? | CLB Card Unhealthy | [9 empty] | 5543
SV104-11038 |  |  |  | Resistor fails-open and than fault occurs that engages CLB | BJT will be permanently turned OFF. Input power path will be broken. No output available at HV transformer board. | If CLB is open, power failure occur and system is in injection and due to iiSC fault now faulty MVAR cannot be bypassed so system will transit to monitoring mode. System cannot go to injection anymore until the fault is cleared. | System will lose injection capability until the MVAR fault is cleared. | 4 | Over voltage. Over Temperature. Over stress due to shock or vibration. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 4 | HALT. Electrical Stress Testing. Thermal Stress Testing. | Failure will be detected by firmware by verifying the CARD_HEALTHY feedback (High when power fails). | 2 | 8 | CLB03? | CLB Card Unhealthy | [9 empty] | 11038
SV104 - 5544 |  |  |  | Resistor fails-short. | 24V will be replicated at the emitter for the shorted duration, on-board ICs may get burn due to this over-voltage. BJT will eventually fail-open due to over-current. Input power path will be broken. No output available at HV transformer board. | On Power failure CLB will retain its state. If particular MVAR is in injection and then power failure of its CLB occurs then it will not effect operation and system will remain in injection. If particular MVAR is bypassed its CLB is closed and system is injecting with reduced MVAR and then power failure occurs on closed CLB then system will retain its state and keeps injecting with reduced MVAR. | System will keep working normally. If CLB is stuck in closed state then system will keep injecting with reduced MVAR. . | 2 | Wear-out due to extensive use. Excessive humidity. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | Failure will be detected by firmware by verifying the CARD_HEALTHY feedback (High when power fails). | 2 | 4 | CLB03? | CLB Card Unhealthy | [9 empty] | 5544
SV104-11039 |  |  |  | Resistor fails-short. and then fault occurs that engages CLB. | 25 V will be replicated at the emitter for the shorted duration, on-board ICs may get burn due to this over-voltage. BJT will eventually fail-open due to over-current. Input power path will be broken. No output available at HV transformer board. | If CLB is open, power failure occur and system is in injection and due to iiSC fault now faulty MVAR cannot be bypassed so system will transit to monitoring mode. System cannot go to injection anymore until the fault is cleared. | System will lose injection capability until the MVAR fault is cleared. | 4 | Wear-out due to extensive use. Excessive humidity. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 4 | HALT. Electrical Stress Testing. Thermal Stress Testing. | Failure will be detected by firmware by verifying the CARD_HEALTHY feedback (High when power fails). | 2 | 8 | CLB03? | CLB Card Unhealthy | [9 empty] | 11039
SV104 - 5545 | Freewheeling Diode. Repeated |  | To provide reverser current flow path. | Diode fails-open. | No path will be available for reverse current to flow. Potential difference creation across BJT can damage the BJT. Input power path will be broken. No output available at HV transformer board. | On Power failure CLB will retain its state. If particular MVAR is in injection and then power failure of its CLB occurs then it will not effect operation and system will remain in injection. If particular MVAR is bypassed its CLB is closed and system is injecting with reduced MVAR and then power failure occurs on closed CLB then system will retain its state and keeps injecting with reduced MVAR. | System will keep working normally. If CLB is stuck in closed state then system will keep injecting with reduced MVAR. . | 2 | Excessive forward current flow. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | Failure will be detected by firmware by verifying the CARD_HEALTHY feedback (High when power fails). | 2 | 4 | CLB03? | CLB Card Unhealthy | [9 empty] | 5545
SV104 - 5546 |  |  |  | Diode fails-short. | An emitter to collector short on BJT will cause the BJT to over-heat and may fail-open. Input power path will be broken. No output available at HV transformer board. and then fault occurs that engages CLB. | On Power failure CLB will retain its state. If particular MVAR is in injection and then power failure of its CLB occurs then it will not effect operation and system will remain in injection. If particular MVAR is bypassed its CLB is closed and system is injecting with reduced MVAR and then power failure occurs on closed CLB then system will retain its state and keeps injecting with reduced MVAR. | System will keep working normally. If CLB is stuck in closed state then system will keep injecting with reduced MVAR. . | 2 | Large reverse voltage. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | Failure will be detected by firmware by verifying the CARD_HEALTHY feedback (High when power fails). | 2 | 4 | CLB03? | CLB Card Unhealthy | [9 empty] | 5546
SV104 - 5547 | 15 V Rail Output Side Capacitors. | C22,C19,C20 | To stable output voltage and to suppress ripples. | Capacitor fails-open. | No immediate effect on board.. | If no other failure is observed on the board, CLB driver board will stay powered. Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | Mechanical stress. Localized heating for long time will separate end connection of capacitor. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [11 empty] | 5547
SV104 - 5548 |  |  |  | Capacitor fails-short. | 15 V power supply will be shorted to ground. PWM controller and gate drivers will not power up. No output available at HV transformer board. | On Power failure CLB will retain its state. If particular MVAR is in injection and then power failure of its CLB occurs then it will not effect operation and system will remain in injection. If particular MVAR is bypassed its CLB is closed and system is injecting with reduced MVAR and then power failure occurs on closed CLB then system will retain its state and keeps injecting with reduced MVAR. | System will keep working normally. If CLB is stuck in closed state then system will keep injecting with reduced MVAR. . | 2 | Wear-out due to dielectric degradation. High-voltage transients. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | Failure will be detected by firmware by verifying the CARD_HEALTHY feedback (High when power fails). | 2 | 4 | CLB03? | CLB Card Unhealthy | [9 empty] | 5548
SV104-11040 |  |  |  | Capacitor fails-short and then fault occurs that engages CLB. | 15 V power supply will be shorted to ground. PWM controller and gate drivers will not power up. No output available at HV transformer board. | If CLB is open, power failure occur and system is in injection and due to iiSC fault now faulty MVAR cannot be bypassed so system will transit to monitoring mode. System cannot go to injection anymore until the fault is cleared. | System will lose injection capability until the MVAR fault is cleared. | 4 | Wear-out due to dielectric degradation. High-voltage transients. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 4 | HALT. Electrical Stress Testing. Thermal Stress Testing. | Failure will be detected by firmware by verifying the CARD_HEALTHY feedback (High when power fails). | 2 | 8 | CLB03? | CLB Card Unhealthy | [9 empty] | 11040
SV104 - 5549 | 24 V Feedback Signal Side Resistor Divider. | R38 | To provide 24 V sensing feedback path. | Resistor fails-open. | 15 V regulator will keep on working from input side and will not turn off. Which will heat up the resistor on MOSFET Q6 drain and will burn out eventually. No output available at HV transformer board. | On Power failure CLB will retain its state. If particular MVAR is in injection and then power failure of its CLB occurs then it will not effect operation and system will remain in injection. If particular MVAR is bypassed its CLB is closed and system is injecting with reduced MVAR and then power failure occurs on closed CLB then system will retain its state and keeps injecting with reduced MVAR. | System will keep working normally. If CLB is stuck in closed state then system will keep injecting with reduced MVAR. . | 2 | Over voltage. Over Temperature. Over stress due to shock or vibration. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | Failure will be detected by firmware by verifying the CARD_HEALTHY feedback (High when power fails). | 2 | 4 | CLB03? | CLB Card Unhealthy | [7 empty] | 0 |  | 5549
SV104-11041 |  |  |  | Resistor fails-open and then fault occurs that engages CLB. | 15 V regulator will keep on working from input side and will not turn off. Which will heat up the resistor on MOSFET Q6 drain and will burn out eventually. No output available at HV transformer board. | If CLB is open, power failure occur and system is in injection and due to iiSC fault now faulty MVAR cannot be bypassed so system will transit to monitoring mode. System cannot go to injection anymore until the fault is cleared. | System will lose injection capability until the MVAR fault is cleared. | 4 | Over voltage. Over Temperature. Over stress due to shock or vibration. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 4 | HALT. Electrical Stress Testing. Thermal Stress Testing. | Failure will be detected by firmware by verifying the CARD_HEALTHY feedback (High when power fails). | 2 | 8 | CLB03? | CLB Card Unhealthy | [9 empty] | 11041
SV104 - 5550 |  |  |  | Resistor fails-short. | Over-current will cause the resistor to eventually fail-open. 15 V regulator will keep on working from input side and will not turn off. Which will heat up the resistor on MOSFET Q6 drain and will burn out eventually. No output available at HV transformer board. | On Power failure CLB will retain its state. If particular MVAR is in injection and then power failure of its CLB occurs then it will not effect operation and system will remain in injection. If particular MVAR is bypassed its CLB is closed and system is injecting with reduced MVAR and then power failure occurs on closed CLB then system will retain its state and keeps injecting with reduced MVAR. | System will keep working normally. If CLB is stuck in closed state then system will keep injecting with reduced MVAR. . | 2 | Wear-out due to extensive use. Excessive humidity. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Conformal Coating. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. Environmental Testing. | Failure will be detected by firmware by verifying the CARD_HEALTHY feedback (High when power fails). | 2 | 4 | CLB03? | CLB Card Unhealthy | [9 empty] | 5550
SV104-11042 |  |  |  | Resistor fails-short and then fault occurs that engages CLB. | Over-current will cause the resistor to eventually fail-open. 15 V regulator will keep on working from input side and will not turn off. Which will heat up the resistor on MOSFET Q6 drain and will burn out eventually. No output available at HV transformer board. | If CLB is open, power failure occur and system is in injection and due to iiSC fault now faulty MVAR cannot be bypassed so system will transit to monitoring mode. System cannot go to injection anymore until the fault is cleared. | System will lose injection capability until the MVAR fault is cleared. | 4 | Wear-out due to extensive use. Excessive humidity. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Conformal Coating. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 4 | HALT. Electrical Stress Testing. Thermal Stress Testing. | Failure will be detected by firmware by verifying the CARD_HEALTHY feedback (High when power fails). | 2 | 8 | CLB03? | CLB Card Unhealthy | [9 empty] | 11042
SV104 - 5551 | 24 V Feedback Signal Side 9 V Zener Diode. | D23 | To turn off the startup circuitry once full bridge auxiliary supply exceeds 9.1 V. | Diode fails-open. | 15 V regulator will keep on working from input side and will not turn off. Which will heat up the resistor on MOSFET Q6 drain and will burn out eventually. No output available at HV transformer board. | On Power failure CLB will retain its state. If particular MVAR is in injection and then power failure of its CLB occurs then it will not effect operation and system will remain in injection. If particular MVAR is bypassed its CLB is closed and system is injecting with reduced MVAR and then power failure occurs on closed CLB then system will retain its state and keeps injecting with reduced MVAR. | System will keep working normally. If CLB is stuck in closed state then system will keep injecting with reduced MVAR. . | 2 | Electrical, Mechanical or environmental overstress. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 2 | 4 | HALT. Electrical Stress Testing. Thermal Stress Testing. | Failure will be detected by firmware by verifying the CARD_HEALTHY feedback (High when power fails). | 2 | 8 | CLB03? | CLB Card Unhealthy | [9 empty] | 5551
SV104-11043 |  |  |  | Diode fails-open and then fault occurs that engages CLB. | 15 V regulator will keep on working from input side and will not turn off. Which will heat up the resistor on MOSFET Q6 drain and will burn out eventually. No output available at HV transformer board. | If CLB is open, power failure occur and system is in injection and due to iiSC fault now faulty MVAR cannot be bypassed so system will transit to monitoring mode. System cannot go to injection anymore until the fault is cleared. | System will lose injection capability until the MVAR fault is cleared. | 4 | Electrical, Mechanical or environmental overstress. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 4 | HALT. Electrical Stress Testing. Thermal Stress Testing. | Failure will be detected by firmware by verifying the CARD_HEALTHY feedback (High when power fails). | 2 | 8 | CLB03? | CLB Card Unhealthy | [9 empty] | 11043
SV104 - 5552 |  |  |  | Diode fails-short. | Startup circuitry will be turned off before full bridge secondary is activated completely. As a result startup circuitry will keep activating and then turn off due to aux voltage. This will eventually damage the startup circuitry of board. No output available at HV transformer board. | On Power failure CLB will retain its state. If particular MVAR is in injection and then power failure of its CLB occurs then it will not effect operation and system will remain in injection. If particular MVAR is bypassed its CLB is closed and system is injecting with reduced MVAR and then power failure occurs on closed CLB then system will retain its state and keeps injecting with reduced MVAR. | System will keep working normally. If CLB is stuck in closed state then system will keep injecting with reduced MVAR. . | 2 | Excessive Temperature. Overcurrent. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 2 | 4 | HALT. Electrical Stress Testing. Thermal Stress Testing. | Failure will be detected by firmware by verifying the CARD_HEALTHY feedback (High when power fails). | 2 | 8 | CLB03? | CLB Card Unhealthy | [9 empty] | 5552
SV104-11044 |  |  |  | Diode fails-short and then fault occurs that engages CLB. | Startup circuitry will be turned off before full bridge secondary is activated completely. As a result startup circuitry will keep activating and then turn off due to aux voltage. This will eventually damage the startup circuitry of board. No output available at HV transformer board. | If CLB is open, power failure occur and system is in injection and due to iiSC fault now faulty MVAR cannot be bypassed so system will transit to monitoring mode. System cannot go to injection anymore until the fault is cleared. | System will lose injection capability until the MVAR fault is cleared. | 4 | Excessive Temperature. Overcurrent. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 4 | HALT. Electrical Stress Testing. Thermal Stress Testing. | Failure will be detected by firmware by verifying the CARD_HEALTHY feedback (High when power fails). | 2 | 8 | CLB03? | CLB Card Unhealthy | [9 empty] | 11044
SV104 - 6977 | 24 V Feedback Signal Side - R39 | R39 | Voltage divider resistor-Low side | Resistor fails-open | No immediate effect on board as Zener will keep voltage regulated at MOSFET gate. This will increase stress on Zener and affect Zener life. Board will stop working if Zener also gets damaged. Board will keep working normally. | If no other failure is observed on the board, CLB driver board will stay powered. Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Over voltage. Over Temperature. Over stress due to shock or vibration. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 10 | [9 empty] | 0 |  | 6977
SV104 - 6978 |  |  |  | Resistor fails-short | 15 V regulator will keep on working from input side and will not turn off. Which will heat up the resistor on MOSFET Q6 drain and will burn out eventually. Startup circuitry will stop working. No output available at HV transformer board. | On Power failure CLB will retain its state. If particular MVAR is in injection and then power failure of its CLB occurs then it will not effect operation and system will remain in injection. If particular MVAR is bypassed its CLB is closed and system is injecting with reduced MVAR and then power failure occurs on closed CLB then system will retain its state and keeps injecting with reduced MVAR. | System will keep working normally. If CLB is stuck in closed state then system will keep injecting with reduced MVAR. . | 2 | Wear-out due to extensive use. Excessive humidity. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | Failure will be detected by firmware by verifying the CARD_HEALTHY feedback (High when power fails). | 2 | 4 | CLB03? | CLB Card Unhealthy | [9 empty] | 6978
SV104-11045 |  |  |  | Resistor fails-short and then fault occurs that engages CLB. | 15 V regulator will keep on working from input side and will not turn off. Which will heat up the resistor on MOSFET Q6 drain and will burn out eventually. Startup circuitry will stop working. No output available at HV transformer board. | If CLB is open, power failure occur and system is in injection and due to iiSC fault now faulty MVAR cannot be bypassed so system will transit to monitoring mode. System cannot go to injection anymore until the fault is cleared. | System will lose injection capability until the MVAR fault is cleared. | 4 | Wear-out due to extensive use. Excessive humidity. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 4 | HALT. Electrical Stress Testing. Thermal Stress Testing. | Failure will be detected by firmware by verifying the CARD_HEALTHY feedback (High when power fails). | 2 | 8 | CLB03? | CLB Card Unhealthy | [7 empty] | 0 |  | 11045
SV104 - 6979 | 24 V Feedback Signal Side - D25 | D25 | To set UVLO to disable startup circuitry | Diode fails-open | 15 V regulator will keep on working from input side and will not turn off. Which will heat up the resistor on MOSFET Q6 drain and will burn out eventually. No output available at HV transformer board. | On Power failure CLB will retain its state. If particular MVAR is in injection and then power failure of its CLB occurs then it will not effect operation and system will remain in injection. If particular MVAR is bypassed its CLB is closed and system is injecting with reduced MVAR and then power failure occurs on closed CLB then system will retain its state and keeps injecting with reduced MVAR. | System will keep working normally. If CLB is stuck in closed state then system will keep injecting with reduced MVAR. . | 2 | Excessive forward current flow. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | Failure will be detected by firmware by verifying the CARD_HEALTHY feedback (High when power fails). | 2 | 4 | CLB03? | CLB Card Unhealthy | [9 empty] | 6979
SV104-11046 |  |  |  | Diode fails-open and then fault occurs that engages CLB. | 15 V regulator will keep on working from input side and will not turn off. Which will heat up the resistor on MOSFET Q6 drain and will burn out eventually. No output available at HV transformer board. | If CLB is open, power failure occur and system is either in monitoring or injection and due to iiSC fault now faulty MVAR cannot be bypassed so system will transit to monitoring mode if injection is going on. System cannot go to injection anymore until the fault is cleared. | System will lose injection capability until the MVAR fault is cleared. | 4 | Excessive forward current flow. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 4 | HALT. Electrical Stress Testing. Thermal Stress Testing. | Failure will be detected by firmware by verifying the CARD_HEALTHY feedback (High when power fails). | 2 | 8 | CLB03? | CLB Card Unhealthy | [7 empty] | 0 |  | 11046
SV104 - 6980 |  |  |  | Diode fails-short | Board will not power up as startup circuit will remain off. Q6 will remain permanently off. No output available at HV transformer board. | On Power failure CLB will retain its state. If particular MVAR is in injection and then power failure of its CLB occurs then it will not effect operation and system will remain in injection. If particular MVAR is bypassed its CLB is closed and system is injecting with reduced MVAR and then power failure occurs on closed CLB then system will retain its state and keeps injecting with reduced MVAR. | System will keep working normally. If CLB is stuck in closed state then system will keep injecting with reduced MVAR. . | 1 | Large reverse voltage. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | Failure will be detected by firmware by verifying the CARD_HEALTHY feedback (High when power fails). | 2 | 2 | CLB03? | CLB Card Unhealthy | [7 empty] | 0 |  | 6980
SV104-11047 |  |  |  | Diode fails-short and then fault occurs that engages CLB. | Board will not power up as startup circuit will remain off. Q6 will remain permanently off. No output available at HV transformer board. | If CLB is open, power failure occur and system is either in monitoring or injection and due to iiSC fault now faulty MVAR cannot be bypassed so system will transit to monitoring mode if injection is going on. System cannot go to injection anymore until the fault is cleared. | System will lose injection capability until the MVAR fault is cleared. | 4 | Large reverse voltage. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 4 | HALT. Electrical Stress Testing. Thermal Stress Testing. | Failure will be detected by firmware by verifying the CARD_HEALTHY feedback (High when power fails). | 2 | 8 | CLB03? | CLB Card Unhealthy | [9 empty] | 11047
SV104 - 6981 | 24 V Feedback Signal Side - D24 | D24 | To prevent reverse power flow from startup circuitry | Diode fails-open | As soon as auxiliary will develop board will be disabled and power-up again and this cycle will keep repeating which will damage the startup circuitry permanently. No output available at HV transformer board. | On Power failure CLB will retain its state. If particular MVAR is in injection and then power failure of its CLB occurs then it will not effect operation and system will remain in injection. If particular MVAR is bypassed its CLB is closed and system is injecting with reduced MVAR and then power failure occurs on closed CLB then system will retain its state and keeps injecting with reduced MVAR. | System will keep working normally. If CLB is stuck in closed state then system will keep injecting with reduced MVAR. . | 2 | Excessive forward current flow. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | Failure will be detected by firmware by verifying the CARD_HEALTHY feedback (High when power fails). | 2 | 4 | CLB03? | CLB Card Unhealthy | [9 empty] | 6981
SV104-11048 |  |  |  | Diode fails-open and then fault occurs that engages CLB. | As soon as auxiliary will develop board will be disabled and power-up again and this cycle will keep repeating which will damage the startup circuitry permanently. No output available at HV transformer board. | If CLB is open, power failure occur and system is in injection and due to iiSC fault now faulty MVAR cannot be bypassed so system will transit to monitoring mode. System cannot go to injection anymore until the fault is cleared. | System will lose injection capability until the MVAR fault is cleared. | 4 | Excessive forward current flow. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 4 | HALT. Electrical Stress Testing. Thermal Stress Testing. | Failure will be detected by firmware by verifying the CARD_HEALTHY feedback (High when power fails). | 2 | 8 | CLB03? | CLB Card Unhealthy | [9 empty] | 11048
SV104 - 6982 |  |  |  | Diode fails-short | Startup circuitry will disable itself before powering up the board. It will happen repeatedly eventually damaging the startup circuitry. No output available at HV transformer board. | On Power failure CLB will retain its state. If particular MVAR is in injection and then power failure of its CLB occurs then it will not effect operation and system will remain in injection. If particular MVAR is bypassed its CLB is closed and system is injecting with reduced MVAR and then power failure occurs on closed CLB then system will retain its state and keeps injecting with reduced MVAR. | System will keep working normally. If CLB is stuck in closed state then system will keep injecting with reduced MVAR. . | 2 | Large reverse voltage. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | Failure will be detected by firmware by verifying the CARD_HEALTHY feedback (High when power fails). | 2 | 4 | CLB03? | CLB Card Unhealthy | [7 empty] | 0 |  | 6982
SV104-11049 |  |  |  | Diode fails-short and then fault occurs that engages CLB. | Startup circuitry will disable itself before powering up the board. It will happen repeatedly eventually damaging the startup circuitry. No output available at HV transformer board. | If CLB is open, power failure occur and system is in injection and due to iiSC fault now faulty MVAR cannot be bypassed so system will transit to monitoring mode. System cannot go to injection anymore until the fault is cleared. | System will lose injection capability until the MVAR fault is cleared. | 4 | Large reverse voltage. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 4 | HALT. Electrical Stress Testing. Thermal Stress Testing. | Failure will be detected by firmware by verifying the CARD_HEALTHY feedback (High when power fails). | 2 | 8 | CLB03? | CLB Card Unhealthy | [9 empty] | 11049
SV104 - 6983 | 24 V Feedback Signal Side - D26 | D26 | Overvoltage protection for MOSFET | Diode fails-open | No immediate effect on board. | If no other failure is observed on the board, CLB driver board will stay powered. Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | Excessive forward current flow. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 2 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 10 | [11 empty] | 6983
SV104 - 6984 |  |  |  | Diode fails-short | 15 V regulator will keep on working from input side and will not turn off. Which will heat up the resistor on MOSFET Q6 drain and will burn out eventually. No output available at HV transformer board. | On Power failure CLB will retain its state. If particular MVAR is in injection and then power failure of its CLB occurs then it will not effect operation and system will remain in injection. If particular MVAR is bypassed its CLB is closed and system is injecting with reduced MVAR and then power failure occurs on closed CLB then system will retain its state and keeps injecting with reduced MVAR. | System will keep working normally. If CLB is stuck in closed state then system will keep injecting with reduced MVAR. . | 2 | Large reverse voltage. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 2 | 4 | HALT. Electrical Stress Testing. Thermal Stress Testing. | Failure will be detected by firmware by verifying the CARD_HEALTHY feedback (High when power fails). | 2 | 8 | CLB03? | CLB Card Unhealthy | [9 empty] | 6984
SV104-11050 |  |  |  | Diode fails-short and then fault occurs that engages CLB. | 15 V regulator will keep on working from input side and will not turn off. Which will heat up the resistor on MOSFET Q6 drain and will burn out eventually. No output available at HV transformer board. | If CLB is open, power failure occur and system is in injection and due to iiSC fault now faulty MVAR cannot be bypassed so system will transit to monitoring mode. System cannot go to injection anymore until the fault is cleared. | System will lose injection capability until the MVAR fault is cleared. | 4 | Large reverse voltage. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 2 | 8 | HALT. Electrical Stress Testing. Thermal Stress Testing. | Failure will be detected by firmware by verifying the CARD_HEALTHY feedback (High when power fails). | 2 | 16 | CLB03? | CLB Card Unhealthy | [7 empty] | 0 |  | 11050
SV104 - 5553 | 24 V Feedback Signal Side MOSFET. | Q7 | To turn OFF power flow controlling MOSFET when auxiliary voltage develops. | MOSFET fails-open | 15 V regulator will keep on working from input side and will not turn off. Which will heat up the resistor on MOSFET Q6 drain and will burn out eventually. No output available at HV transformer board. | On Power failure CLB will retain its state. If particular MVAR is in injection and then power failure of its CLB occurs then it will not effect operation and system will remain in injection. If particular MVAR is bypassed its CLB is closed and system is injecting with reduced MVAR and then power failure occurs on closed CLB then system will retain its state and keeps injecting with reduced MVAR. | System will keep working normally. If CLB is stuck in closed state then system will keep injecting with reduced MVAR. . | 2 | Overheating Mechanical stress resulting in cracked MOSFET body. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | Failure will be detected by firmware by verifying the CARD_HEALTHY feedback (High when power fails). | 2 | 4 | CLB03? | CLB Card Unhealthy | [9 empty] | 5553
SV104-11051 |  |  |  | MOSFET fails-open and then fault occurs that engages CLB. | 15 V regulator will keep on working from input side and will not turn off. Which will heat up the resistor on MOSFET Q6 drain and will burn out eventually. No output available at HV transformer board. | If CLB is open, power failure occur and system is in injection and due to iiSC fault now faulty MVAR cannot be bypassed so system will transit to monitoring mode. System cannot go to injection anymore until the fault is cleared. | System will lose injection capability until the MVAR fault is cleared. | 4 | Overheating Mechanical stress resulting in cracked MOSFET body. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 4 | HALT. Electrical Stress Testing. Thermal Stress Testing. | Failure will be detected by firmware by verifying the CARD_HEALTHY feedback (High when power fails). | 2 | 8 | CLB03? | CLB Card Unhealthy | [9 empty] | 11051
SV104 - 5554 |  |  |  | MOSFET fails-short. | Startup circuitry will remain off permanently as Q6 remains off permanently. 15 V regulator will keep on working from input side and will not turn off. Which will heat up the resistor on MOSFET Q6 drain and will burn out eventually. No output available at HV transformer board. | On Power failure CLB will retain its state. If particular MVAR is in injection and then power failure of its CLB occurs then it will not effect operation and system will remain in injection. If particular MVAR is bypassed its CLB is closed and system is injecting with reduced MVAR and then power failure occurs on closed CLB then system will retain its state and keeps injecting with reduced MVAR. | System will keep working normally. If CLB is stuck in closed state then system will keep injecting with reduced MVAR. . | 2 | Transients Overheating as a result of loose connection with heat sink Overcurrent Counterfeit part Damage during mechanical assembly of board Metallic debris stuck in between terminals | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | Failure will be detected by firmware by verifying the CARD_HEALTHY feedback (High when power fails). | 2 | 4 | CLB03? | CLB Card Unhealthy | [9 empty] | 5554
SV104-11052 |  |  |  | MOSFET fails-short and then fault occurs that engages CLB. | Startup circuitry will remain off permanently as Q6 remains off permanently. 15 V regulator will keep on working from input side and will not turn off. Which will heat up the resistor on MOSFET Q6 drain and will burn out eventually. No output available at HV transformer board. | If CLB is open, power failure occur and system is in injection and due to iiSC fault now faulty MVAR cannot be bypassed so system will transit to monitoring mode. System cannot go to injection anymore until the fault is cleared. | System will lose injection capability until the MVAR fault is cleared. | 4 | Transients Overheating as a result of loose connection with heat sink Overcurrent Counterfeit part Damage during mechanical assembly of board Metallic debris stuck in between terminals | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 4 | HALT. Electrical Stress Testing. Thermal Stress Testing. | Failure will be detected by firmware by verifying the CARD_HEALTHY feedback (High when power fails). | 2 | 8 | CLB03? | CLB Card Unhealthy | [7 empty] | 0 |  | 11052
SV104 - 5555 | 24 V Feedback Signal Side MOSFET.- Zener at Gate | D25 | To protect MOSFET gate from over-voltage. | Diode fails-open. | Over-voltage protection of MOSFET won't be available. No immediate effect on board in normal operations. | If no other failure is observed on the board, CLB driver board will stay powered. Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | Excessive forward current flow. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [11 empty] | 5555
SV104 - 5556 |  |  |  | Diode fails-short. | Board will not power up as startup circuit will remain off. Q6 will remain permanently off. No output available at HV transformer board. | On Power failure CLB will retain its state. If particular MVAR is in injection and then power failure of its CLB occurs then it will not effect operation and system will remain in injection. If particular MVAR is bypassed its CLB is closed and system is injecting with reduced MVAR and then power failure occurs on closed CLB then system will retain its state and keeps injecting with reduced MVAR. | System will keep working normally. If CLB is stuck in closed state then system will keep injecting with reduced MVAR. . | 2 | Large reverse voltage. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | Failure will be detected by firmware by verifying the CARD_HEALTHY feedback (High when power fails). | 2 | 4 | CLB03? | CLB Card Unhealthy | [9 empty] | 5556
SV104-11053 |  |  |  | Diode fails-short and then fault occurs that engages CLB. | Board will not power up as startup circuit will remain off. Q6 will remain permanently off. No output available at HV transformer board. | If CLB is open, power failure occur and system is in injection and due to iiSC fault now faulty MVAR cannot be bypassed so system will transit to monitoring mode. System cannot go to injection anymore until the fault is cleared. | System will lose injection capability until the MVAR fault is cleared. | 4 | Large reverse voltage. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 4 | HALT. Electrical Stress Testing. Thermal Stress Testing. | Failure will be detected by firmware by verifying the CARD_HEALTHY feedback (High when power fails). | 2 | 8 | CLB03? | CLB Card Unhealthy | [9 empty] | 11053
| PWM Controller | [26 empty] | 0
SV104 - 5557 | PWM Controller IC. | U1 | To provide alternate PWM pulses for full bridge gate driver. | IC output is permanently low. | No PWM will be available for half bridge driver ICs, No output available at HV transformer board. | On Power failure CLB will retain its state. If particular MVAR is in injection and then power failure of its CLB occurs then it will not effect operation and system will remain in injection. If particular MVAR is bypassed its CLB is closed and system is injecting with reduced MVAR and then power failure occurs on closed CLB then system will retain its state and keeps injecting with reduced MVAR. | System will keep working normally. If CLB is stuck in closed state then system will keep injecting with reduced MVAR. . | 2 | Electrical Overstress. ESD. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | Failure will be detected by firmware by verifying the CARD_HEALTHY feedback (High when power fails). | 2 | 4 | CLB03? | CLB Card Unhealthy | [9 empty] | 5557
SV104-11054 |  |  |  | IC output is permanently low and then fault occurs that engages CLB. | No PWM will be available for half bridge driver ICs, No output available at HV transformer board. | If CLB is open, power failure occur and system is in injection and due to iiSC fault now faulty MVAR cannot be bypassed so system will transit to monitoring mode. System cannot go to injection anymore until the fault is cleared. | System will lose injection capability until the MVAR fault is cleared. | 4 | Electrical Overstress. ESD. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 4 | HALT. Electrical Stress Testing. Thermal Stress Testing. | Failure will be detected by firmware by verifying the CARD_HEALTHY feedback (High when power fails). | 2 | 8 | CLB03? | CLB Card Unhealthy | [7 empty] | 0 |  | 11054
SV104 - 5558 |  |  |  | One of output is permanently high. | Output of Full Bridge circuit will be 12 V at no load. HV transformer board will have no output as soon as load is applied. | On Power failure CLB will retain its state. If particular MVAR is in injection and then power failure of its CLB occurs then it will not effect operation and system will remain in injection. If particular MVAR is bypassed its CLB is closed and system is injecting with reduced MVAR and then power failure occurs on closed CLB then system will retain its state and keeps injecting with reduced MVAR. | System will keep working normally. If CLB is stuck in closed state then system will keep injecting with reduced MVAR. . | 2 | Electrical Overstress. ESD. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | Failure will be detected by firmware by verifying the CARD_HEALTHY feedback (High when power fails). | 2 | 4 | CLB03? | CLB Card Unhealthy | [9 empty] | 5558
SV104-11055 |  |  |  | One of output is permanently high and then fault occurs that engages CLB. | Output of Full Bridge circuit will be 12 V at no load. HV transformer board will have no output as soon as load is applied. | If CLB is open, power failure occur and system is in injection and due to iiSC fault now faulty MVAR cannot be bypassed so system will transit to monitoring mode. System cannot go to injection anymore until the fault is cleared. | System will lose injection capability until the MVAR fault is cleared. | 4 | Electrical Overstress. ESD. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 4 | HALT. Electrical Stress Testing. Thermal Stress Testing. | Failure will be detected by firmware by verifying the CARD_HEALTHY feedback (High when power fails). | 2 | 8 | CLB03? | CLB Card Unhealthy | [9 empty] | 11055
SV104 - 5559 |  |  |  | PWM is having different duty cycle than desired. | Output of Full Bridge circuit will have different duty cycle. HV transformer board will have more or less than 24 V output. | If no other failure is observed on the board, CLB driver board will stay powered. Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | Internal IC damage. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 2 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 10 | [9 empty] | 0 |  | 5559
SV104 - 5560 | Line Under-Voltage Lockout Voltage Divider High Side Resistor. | R1 | To turn OFF gate driver PWM in case of under-voltage. | Resistor fails-open. | PWM controller will remain off permanently. No output available for HV transformer board. | On Power failure CLB will retain its state. If particular MVAR is in injection and then power failure of its CLB occurs then it will not effect operation and system will remain in injection. If particular MVAR is bypassed its CLB is closed and system is injecting with reduced MVAR and then power failure occurs on closed CLB then system will retain its state and keeps injecting with reduced MVAR. | System will keep working normally. If CLB is stuck in closed state then system will keep injecting with reduced MVAR. . | 2 | Over voltage. Over Temperature. Over stress due to shock or vibration. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | Failure will be detected by firmware by verifying the CARD_HEALTHY feedback (High when power fails). | 2 | 4 | CLB03? | CLB Card Unhealthy | [9 empty] | 5560
SV104-11056 |  |  |  | Resistor fails-open and then fault occurs that engages CLB. | PWM controller will remain off permanently. No output available for HV transformer board. | If CLB is open, power failure occur and system is in injection and due to iiSC fault now faulty MVAR cannot be bypassed so system will transit to monitoring mode. System cannot go to injection anymore until the fault is cleared. | System will lose injection capability until the MVAR fault is cleared. | 4 | Over voltage. Over Temperature. Over stress due to shock or vibration. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 4 | HALT. Electrical Stress Testing. Thermal Stress Testing. | Failure will be detected by firmware by verifying the CARD_HEALTHY feedback (High when power fails). | 2 | 8 | CLB03? | CLB Card Unhealthy | [9 empty] | 11056
SV104 - 5561 |  |  |  | Resistor fails-short. | UVLO pin will get damaged, No PWM will be available for half bridge driver ICs, No output available at HV transformer board. | On Power failure CLB will retain its state. If particular MVAR is in injection and then power failure of its CLB occurs then it will not effect operation and system will remain in injection. If particular MVAR is bypassed its CLB is closed and system is injecting with reduced MVAR and then power failure occurs on closed CLB then system will retain its state and keeps injecting with reduced MVAR. | System will keep working normally. If CLB is stuck in closed state then system will keep injecting with reduced MVAR. . | 2 | Wear-out due to extensive use. Excessive humidity. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | Failure will be detected by firmware by verifying the CARD_HEALTHY feedback (High when power fails). | 2 | 4 | CLB03? | CLB Card Unhealthy | [9 empty] | 5561
SV104-11057 |  |  |  | Resistor fails-short and then fault occurs that engages CLB. | UVLO pin will get damaged, No PWM will be available for half bridge driver ICs, No output available at HV transformer board. | If CLB is open, power failure occur and system is in injection and due to iiSC fault now faulty MVAR cannot be bypassed so system will transit to monitoring mode. System cannot go to injection anymore until the fault is cleared. | System will lose injection capability until the MVAR fault is cleared. | 4 | Wear-out due to extensive use. Excessive humidity. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 4 | HALT. Electrical Stress Testing. Thermal Stress Testing. | Failure will be detected by firmware by verifying the CARD_HEALTHY feedback (High when power fails). | 2 | 8 | CLB03? | CLB Card Unhealthy | [7 empty] | 0 |  | 11057
SV104 - 5562 | Line Under-Voltage Lockout Voltage Divider Low Side Resistor. | R13 | To turn OFF gate driver PWM in case of under-voltage. | Resistor fails-open. | UVLO pin will get damaged, No PWM will be available for half bridge driver ICs, No output available at HV transformer board. | On Power failure CLB will retain its state. If particular MVAR is in injection and then power failure of its CLB occurs then it will not effect operation and system will remain in injection. If particular MVAR is bypassed its CLB is closed and system is injecting with reduced MVAR and then power failure occurs on closed CLB then system will retain its state and keeps injecting with reduced MVAR. | System will keep working normally. If CLB is stuck in closed state then system will keep injecting with reduced MVAR. . | 2 | Over voltage. Over Temperature. Over stress due to shock or vibration. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | Failure will be detected by firmware by verifying the CARD_HEALTHY feedback (High when power fails). | 2 | 4 | CLB03? | CLB Card Unhealthy | [9 empty] | 5562
SV104-11058 |  |  |  | Resistor fails-open and then fault occurs that engages CLB. | UVLO pin will get damaged, No PWM will be available for half bridge driver ICs, No output available at HV transformer board. | If CLB is open, power failure occur and system is in injection and due to iiSC fault now faulty MVAR cannot be bypassed so system will transit to monitoring mode. System cannot go to injection anymore until the fault is cleared. | System will lose injection capability until the MVAR fault is cleared. | 4 | Over voltage. Over Temperature. Over stress due to shock or vibration. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 4 | HALT. Electrical Stress Testing. Thermal Stress Testing. | Failure will be detected by firmware by verifying the CARD_HEALTHY feedback (High when power fails). | 2 | 8 | CLB03? | CLB Card Unhealthy | [7 empty] | 0 |  | 11058
SV104 - 5563 |  |  |  | Resistor fails-short. | PWM controller will remain off permanently. No output available. | On Power failure CLB will retain its state. If particular MVAR is in injection and then power failure of its CLB occurs then it will not effect operation and system will remain in injection. If particular MVAR is bypassed its CLB is closed and system is injecting with reduced MVAR and then power failure occurs on closed CLB then system will retain its state and keeps injecting with reduced MVAR. | System will keep working normally. If CLB is stuck in closed state then system will keep injecting with reduced MVAR. . | 2 | Wear-out due to extensive use. Excessive humidity. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | Failure will be detected by firmware by verifying the CARD_HEALTHY feedback (High when power fails). | 2 | 4 | CLB03? | CLB Card Unhealthy | [9 empty] | 5563
SV104-11059 |  |  |  | Resistor fails-short and then fault occurs that engages CLB. | PWM controller will remain off permanently. No output available. | If CLB is open, power failure occur and system is in injection and due to iiSC fault now faulty MVAR cannot be bypassed so system will transit to monitoring mode. System cannot go to injection anymore until the fault is cleared. | System will lose injection capability until the MVAR fault is cleared. | 4 | Wear-out due to extensive use. Excessive humidity. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 4 | HALT. Electrical Stress Testing. Thermal Stress Testing. | Failure will be detected by firmware by verifying the CARD_HEALTHY feedback (High when power fails). | 2 | 8 | CLB03? | CLB Card Unhealthy | [9 empty] | 11059
SV104 - 5564 | RT2 Biasing Resistor. | R14 | To control oscillator dead time. | Resistor fails-open. | Dead time between alternating PWMs will be altered (maximum). 1 PWM will be permanently high, while other will be permanently low. Output of isolation transformer will not be available. No output available at HV transformer board. | On Power failure CLB will retain its state. If particular MVAR is in injection and then power failure of its CLB occurs then it will not effect operation and system will remain in injection. If particular MVAR is bypassed its CLB is closed and system is injecting with reduced MVAR and then power failure occurs on closed CLB then system will retain its state and keeps injecting with reduced MVAR. | System will keep working normally. If CLB is stuck in closed state then system will keep injecting with reduced MVAR. . | 2 | Over voltage. Over Temperature. Over stress due to shock or vibration. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | Failure will be detected by firmware by verifying the CARD_HEALTHY feedback (High when power fails). | 2 | 4 | CLB03? | CLB Card Unhealthy | [9 empty] | 5564
SV104-11060 |  |  |  | Resistor fails-open and then fault occurs that engages CLB. | Dead time between alternating PWMs will be altered (maximum). 1 PWM will be permanently high, while other will be permanently low. Output of isolation transformer will not be available. No output available at HV transformer board. | If CLB is open, power failure occur and system is in injection and due to iiSC fault now faulty MVAR cannot be bypassed so system will transit to monitoring mode. System cannot go to injection anymore until the fault is cleared. | System will lose injection capability until the MVAR fault is cleared. | 4 | Over voltage. Over Temperature. Over stress due to shock or vibration. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 4 | HALT. Electrical Stress Testing. Thermal Stress Testing. | Failure will be detected by firmware by verifying the CARD_HEALTHY feedback (High when power fails). | 2 | 8 | CLB03? | CLB Card Unhealthy | [9 empty] | 11060
SV104 - 5565 |  |  |  | Resistor fails-short. | Dead time between alternating PWMs will be altered (zero). 1 PWM will be permanently high, while other will be permanently low at the same time. Output of isolation transformer will not be available. No output available at HV transformer board. | On Power failure CLB will retain its state. If particular MVAR is in injection and then power failure of its CLB occurs then it will not effect operation and system will remain in injection. If particular MVAR is bypassed its CLB is closed and system is injecting with reduced MVAR and then power failure occurs on closed CLB then system will retain its state and keeps injecting with reduced MVAR. | System will keep working normally. If CLB is stuck in closed state then system will keep injecting with reduced MVAR. . | 2 | Wear-out due to extensive use. Excessive humidity. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | Failure will be detected by firmware by verifying the CARD_HEALTHY feedback (High when power fails). | 2 | 4 | CLB03? | CLB Card Unhealthy | [7 empty] | 0 |  | 5565
SV104-11061 |  |  |  | Resistor fails-short and then fault occurs that engages CLB. | Dead time between alternating PWMs will be altered (zero). 1 PWM will be permanently high, while other will be permanently low at the same time. Output of isolation transformer will not be available. No output available at HV transformer board. | If CLB is open, power failure occur and system is in injection and due to iiSC fault now faulty MVAR cannot be bypassed so system will transit to monitoring mode. System cannot go to injection anymore until the fault is cleared. | System will lose injection capability until the MVAR fault is cleared. | 4 | Wear-out due to extensive use. Excessive humidity. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 4 | HALT. Electrical Stress Testing. Thermal Stress Testing. | Failure will be detected by firmware by verifying the CARD_HEALTHY feedback (High when power fails). | 2 | 8 | CLB03? | CLB Card Unhealthy | [9 empty] | 11061
SV104 - 5566 | RT1 Biasing Resistor. | R15 | To control oscillator maximum ON time. | Resistor fails-open. | On-time between alternating PWMs will be altered (Zero) The Period of the PWM will be equal to the Dead-Time 1 PWM will be permanently high, while other will be permanently low. Output of isolation transformer will not be available. No output available at HV transformer board. | On Power failure CLB will retain its state. If particular MVAR is in injection and then power failure of its CLB occurs then it will not effect operation and system will remain in injection. If particular MVAR is bypassed its CLB is closed and system is injecting with reduced MVAR and then power failure occurs on closed CLB then system will retain its state and keeps injecting with reduced MVAR. | System will keep working normally. If CLB is stuck in closed state then system will keep injecting with reduced MVAR. . | 2 | Over voltage. Over Temperature. Over stress due to shock or vibration. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | Failure will be detected by firmware by verifying the CARD_HEALTHY feedback (High when power fails). | 2 | 4 | CLB03? | CLB Card Unhealthy | [9 empty] | 5566
SV104-11062 |  |  |  | Resistor fails-open and then fault occurs that engages CLB. | On-time between alternating PWMs will be altered (Zero) The Period of the PWM will be equal to the Dead-Time 1 PWM will be permanently high, while other will be permanently low. Output of isolation transformer will not be available. No output available at HV transformer board. | If CLB is open, power failure occur and system is in injection and due to iiSC fault now faulty MVAR cannot be bypassed so system will transit to monitoring mode. System cannot go to injection anymore until the fault is cleared. | System will lose injection capability until the MVAR fault is cleared. | 4 | Over voltage. Over Temperature. Over stress due to shock or vibration. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 4 | HALT. Electrical Stress Testing. Thermal Stress Testing. | Failure will be detected by firmware by verifying the CARD_HEALTHY feedback (High when power fails). | 2 | 8 | CLB03? | CLB Card Unhealthy | [9 empty] | 11062
SV104 - 5567 |  |  |  | Resistor fails-short. | Dead time between alternating PWMs will be altered (maximum). 1 PWM will be permanently high, while other will be permanently low. Output of isolation transformer will not be available. No output available at HV transformer board. | On Power failure CLB will retain its state. If particular MVAR is in injection and then power failure of its CLB occurs then it will not effect operation and system will remain in injection. If particular MVAR is bypassed its CLB is closed and system is injecting with reduced MVAR and then power failure occurs on closed CLB then system will retain its state and keeps injecting with reduced MVAR. | System will keep working normally. If CLB is stuck in closed state then system will keep injecting with reduced MVAR. . | 2 | Wear-out due to extensive use. Excessive humidity. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | Failure will be detected by firmware by verifying the CARD_HEALTHY feedback (High when power fails). | 2 | 4 | CLB03? | CLB Card Unhealthy | [9 empty] | 5567
SV104-11063 |  |  |  | Resistor fails-short and then fault occurs that engages CLB. | Dead time between alternating PWMs will be altered (maximum). 1 PWM will be permanently high, while other will be permanently low. Output of isolation transformer will not be available. No output available at HV transformer board. | If CLB is open, power failure occur and system is in injection and due to iiSC fault now faulty MVAR cannot be bypassed so system will transit to monitoring mode. System cannot go to injection anymore until the fault is cleared. | System will lose injection capability until the MVAR fault is cleared. | 4 | Over voltage. Over Temperature. Over stress due to shock or vibration. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 4 | HALT. Electrical Stress Testing. Thermal Stress Testing. | Failure will be detected by firmware by verifying the CARD_HEALTHY feedback (High when power fails). | 2 | 8 | CLB03? | CLB Card Unhealthy | [9 empty] | 11063
SV104 - 5568 | Restart Timer Resistor. | R16 | To set PWM restart signal biasing. | Resistor fails-open. | Restart timer functionality will be compromised. No immediate effect on board in normal operations. | If no other failure is observed on the board, CLB driver board will stay powered. Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | Over voltage. Over Temperature. Over stress due to shock or vibration. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [11 empty] | 5568
SV104 - 5569 |  |  |  | Resistor fails-short. | Restart timer functionality will be compromised. No immediate effect on board in normal operations. | If no other failure is observed on the board, CLB driver board will stay powered. Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | Wear-out due to extensive use. Excessive humidity. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [11 empty] | 5569
SV104 - 5570 | Soft-Start Capacitor. | C10 | To provide soft-start biasing value. | Capacitor fails-open. | Soft start functionality will be compromised. No immediate effect on board in normal operations. | If no other failure is observed on the board, CLB driver board will stay powered. Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | Mechanical stress. Localized heating for long time will separate end connection of capacitor. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [11 empty] | 5570
SV104 - 5571 |  |  |  | Capacitor fails-short. | PWM controller will turn off permanently. No output available for board. | On Power failure CLB will retain its state. If particular MVAR is in injection and then power failure of its CLB occurs then it will not effect operation and system will remain in injection. If particular MVAR is bypassed its CLB is closed and system is injecting with reduced MVAR and then power failure occurs on closed CLB then system will retain its state and keeps injecting with reduced MVAR. | System will keep working normally. If CLB is stuck in closed state then system will keep injecting with reduced MVAR. . | 2 | Wear-out due to dielectric degradation. High-voltage transients. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | Failure will be detected by firmware by verifying the CARD_HEALTHY feedback (High when power fails). | 2 | 4 | CLB03? | CLB Card Unhealthy | [9 empty] | 5571
SV104-11064 |  |  |  | Capacitor fails-short and then fault occurs that engages CLB. | PWM controller will turn off permanently. No output available for board. | If CLB is open, power failure occur and system is in injection and due to iiSC fault now faulty MVAR cannot be bypassed so system will transit to monitoring mode. System cannot go to injection anymore until the fault is cleared. | System will lose injection capability until the MVAR fault is cleared. | 4 | Wear-out due to dielectric degradation. High-voltage transients. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 4 | HALT. Electrical Stress Testing. Thermal Stress Testing. | Failure will be detected by firmware by verifying the CARD_HEALTHY feedback (High when power fails). | 2 | 8 | CLB03? | CLB Card Unhealthy | [9 empty] | 11064
SV104 - 5572 | Ramp Control Resistor. | R12 | To provide ramp control of PWM. | Resistor fails-open. | PWM ramp will be affected. Output of Full Bridge circuit will be different than desired. HV transformer board will have more or less than 24 V output. | If no other failure is observed on the board, CLB driver board will stay powered. Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | Over voltage. Over Temperature. Over stress due to shock or vibration. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [11 empty] | 5572
SV104 - 5573 |  |  |  | Resistor fails-short. | PWM ramp will be affected. Output of Full Bridge circuit will be different than desired. HV transformer board will have more or less than 24 V output. | If no other failure is observed on the board, CLB driver board will stay powered. Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | Wear-out due to extensive use. Excessive humidity. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [11 empty] | 5573
SV104 - 5574 | Current Sense Signal Filtration Capacitor. | C12 | To filter the CS signal. | Capacitor fails-open. | No immediate effect. | If no other failure is observed on the board, CLB driver board will stay powered. Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | Electrical, mechanical or environmental overstress. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [11 empty] | 5574
SV104 - 5575 |  |  |  | Capacitor fails-short. | Capacitor will fail-open due to over-current. PWM current limiting functionality will be compromised while the capacitor remains shorted. No immediate effect on board in normal operations. | If no other failure is observed on the board, CLB driver board will stay powered. Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | Wear-out due to dielectric degradation. High-voltage transients. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [11 empty] | 5575
SV104 - 5576 | Current Sense Capacitor. | C9 | To limit PWM current. | Capacitor fails-open. | PWM current limiting functionality will be compromised. No immediate effect on board in normal operations. | If no other failure is observed on the board, CLB driver board will stay powered. Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | Mechanical stress. Localized heating for long time will separate end connection of capacitor. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [11 empty] | 5576
SV104 - 5577 |  |  |  | Capacitor fails-short. | PWM current limiting functionality will be compromised. No immediate effect on board in normal operations. | If no other failure is observed on the board, CLB driver board will stay powered. Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | Wear-out due to dielectric degradation. High-voltage transients. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [11 empty] | 5577
SV104-12403 | Decoupling Capacitor | C11 | To Filter Noise | Capacitor fails-open. | No immediate effect on board in normal operations. | If no other failure is observed on the board, CLB driver board will stay powered. Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | Mechanical stress. Localized heating for long time will separate end connection of capacitor. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. RTV application on edges to stop water ingress. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. Vibration Testing. | None. | 5 | 5 | [11 empty] | 12403
SV104-12404 |  |  |  | Capacitor fails-short. | Internal Reference Voltage will be shorted to ground. PWM output will be disabled. Input Fuse Will be Blown No output available at HV transformer board. | On Power failure CLB will retain its state. If particular MVAR is in injection and then power failure of its CLB occurs then it will not effect operation and system will remain in injection. If particular MVAR is bypassed its CLB is closed and system is injecting with reduced MVAR and then power failure occurs on closed CLB then system will retain its state and keeps injecting with reduced MVAR. | System will keep working normally. If CLB is stuck in closed state then system will keep injecting with reduced MVAR. . | 2 | Wear-out due to dielectric degradation. High-voltage transients. De-gradation of components. Water ingress during humidity condition as it is film capacitor. Overvoltage | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. RTV application on edges to stop water ingress. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. Environmental Testing. | Failure will be detected by firmware by verifying the CARD_HEALTHY feedback (High when power fails). | 2 | 4 | CLB03? | CLB Card Unhealthy | [7 empty] | 0 |  | 12404
SV104-12405 |  |  |  | Capacitor fails-short and then fault occurs that engages CLB. | Internal Reference Voltage will be shorted to ground. PWM output will be disabled. Input Fuse Will be Blown No output available at HV transformer board. | If CLB is open, power failure occur and system is in injection and due to iiSC fault now faulty MVAR cannot be bypassed so system will transit to monitoring mode. System cannot go to injection anymore until the fault is cleared. | System will lose injection capability until the MVAR fault is cleared. | 4 | Wear-out due to dielectric degradation. High-voltage transients. De-gradation of components. Water ingress during humidity condition as it is film capacitor. Overvoltage | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. RTV application on edges to stop water ingress. | 1 | 4 | HALT. Electrical Stress Testing. Thermal Stress Testing. | Failure will be detected by firmware by verifying the CARD_HEALTHY feedback (High when power fails). | 2 | 8 | CLB03? | CLB Card Unhealthy | [9 empty] | 12405
SV104-11065 | Input Filtration Capacitance | C1 | To suppress ripples on input voltage. | Capacitor fails-open. | No immediate effect on board due to presence of multiple capacitors at different stages.. | If no other failure is observed on the board, CLB driver board will stay powered. Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | Mechanical stress. Localized heating for long time will separate end connection of capacitor. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. Vibration Testing. | None. | 5 | 5 | [11 empty] | 11065
SV104-11066 |  |  |  | Capacitor fails-short. | 15V rail will get shorted to ground thus No output available at HV transformer board . | On Power failure CLB will retain its state. If particular MVAR is in injection and then power failure of its CLB occurs then it will not effect operation and system will remain in injection. If particular MVAR is bypassed its CLB is closed and system is injecting with reduced MVAR and then power failure occurs on closed CLB then system will retain its state and keeps injecting with reduced MVAR. | System will keep working normally. If CLB is stuck in closed state then system will keep injecting with reduced MVAR. . | 2 | Wear-out due to dielectric degradation. High-voltage transients. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | Failure will be detected by firmware by verifying the CARD_HEALTHY feedback (High when power fails). | 2 | 4 | CLB03? | CLB Card Unhealthy | [9 empty] | 11066
SV104-12406 |  |  |  | Capacitor fails-short and then fault occurs that engages CLB. | 15V rail will get shorted to ground thus No output available at HV transformer board . | If CLB is open, power failure occur and system is in injection and due to iiSC fault now faulty MVAR cannot be bypassed so system will transit to monitoring mode. System cannot go to injection anymore until the fault is cleared. | System will lose injection capability until the MVAR fault is cleared. | 4 | Wear-out due to dielectric degradation. High-voltage transients. De-gradation of components. Water ingress during humidity condition as it is film capacitor. Overvoltage | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. RTV application on edges to stop water ingress. | 1 | 4 | HALT. Electrical Stress Testing. Thermal Stress Testing. | Failure will be detected by firmware by verifying the CARD_HEALTHY feedback (High when power fails). | 2 | 8 | CLB03? | CLB Card Unhealthy | [9 empty] | 12406
SV104-11067 | Current Sense Resistance | R28 | To Sense Overcurrent | Resistor fails-open. | Overcurrent Protection will be compromised during overcurrent condition at primary. No immediate Effect in normal condition. | If no other failure is observed on the board, CLB driver board will stay powered. Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | Over voltage. Over Temperature. Over stress due to shock or vibration. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [11 empty] | 11067
SV104-11068 |  |  |  | Resistor fails-open and then fault occurs that engages CLB. | IC may trigger False overcurrent and disable output. No output available at HV transformer board | If CLB is open, power failure occur and system is in injection and due to iiSC fault now faulty MVAR cannot be bypassed so system will transit to monitoring mode. System cannot go to injection anymore until the fault is cleared. | System will lose injection capability until the MVAR fault is cleared. | 4 | Over voltage. Over Temperature. Over stress due to shock or vibration. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 4 | HALT. Electrical Stress Testing. Thermal Stress Testing. | Failure will be detected by firmware by verifying the CARD_HEALTHY feedback (High when power fails). | 2 | 8 | CLB03? | CLB Card Unhealthy | [7 empty] | 0 |  | 11068
SV104-11069 |  |  |  | Resistor fails-short. | Over current Threshold will Decrease. IC will trigger False overcurrent and disable output. No output available at HV transformer board | On Power failure CLB will retain its state. If particular MVAR is in injection and then power failure of its CLB occurs then it will not effect operation and system will remain in injection. If particular MVAR is bypassed its CLB is closed and system is injecting with reduced MVAR and then power failure occurs on closed CLB then system will retain its state and keeps injecting with reduced MVAR. | System will keep working normally. If CLB is stuck in closed state then system will keep injecting with reduced MVAR. . | 2 | Wear-out due to extensive use. Excessive humidity. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 10 | CLB03? | CLB Card Unhealthy | [9 empty] | 11069
SV104-11070 |  |  |  | Resistor fails-short and then fault occurs that engages CLB. | Over current Threshold will Decrease. IC will trigger False overcurrent and disable output. No output available at HV transformer board | If CLB is open, power failure occur and system is in injection and due to iiSC fault now faulty MVAR cannot be bypassed so system will transit to monitoring mode. System cannot go to injection anymore until the fault is cleared. | System will lose injection capability until the MVAR fault is cleared. | 4 | Over voltage. Over Temperature. Over stress due to shock or vibration. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 4 | HALT. Electrical Stress Testing. Thermal Stress Testing. | Failure will be detected by firmware by verifying the CARD_HEALTHY feedback (High when power fails). | 2 | 8 | CLB03? | CLB Card Unhealthy | [7 empty] | 0 |  | 11070
SV104 - 5578 | Output Driver Resistor. | R4,R5 | To limit gate driver current. | Resistor fails-open. | Gate driver PWM path will be broken. No output available at HV transformer board. | On Power failure CLB will retain its state. If particular MVAR is in injection and then power failure of its CLB occurs then it will not effect operation and system will remain in injection. If particular MVAR is bypassed its CLB is closed and system is injecting with reduced MVAR and then power failure occurs on closed CLB then system will retain its state and keeps injecting with reduced MVAR. | System will keep working normally. If CLB is stuck in closed state then system will keep injecting with reduced MVAR. . | 2 | Over voltage. Over Temperature. Over stress due to shock or vibration. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | Failure will be detected by firmware by verifying the CARD_HEALTHY feedback (High when power fails). | 2 | 4 | CLB03? | CLB Card Unhealthy | [9 empty] | 5578
SV104-11071 |  |  |  | Resistor fails-open and then fault occurs that engages CLB. | Gate driver PWM path will be broken. No output available at HV transformer board. | If CLB is open, power failure occur and system is in injection and due to iiSC fault now faulty MVAR cannot be bypassed so system will transit to monitoring mode. System cannot go to injection anymore until the fault is cleared. | System will lose injection capability until the MVAR fault is cleared. | 4 | Over voltage. Over Temperature. Over stress due to shock or vibration. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 4 | HALT. Electrical Stress Testing. Thermal Stress Testing. | Failure will be detected by firmware by verifying the CARD_HEALTHY feedback (High when power fails). | 2 | 8 | CLB03? | CLB Card Unhealthy | [7 empty] | 0 |  | 11071
SV104 - 5579 |  |  |  | Resistor fails-short. | No immediate till the shorted duration. Resistor will fail-open due to over-current. Gate driver PWM path will be broken. No output available at HV transformer board. | On Power failure CLB will retain its state. If particular MVAR is in injection and then power failure of its CLB occurs then it will not effect operation and system will remain in injection. If particular MVAR is bypassed its CLB is closed and system is injecting with reduced MVAR and then power failure occurs on closed CLB then system will retain its state and keeps injecting with reduced MVAR. | System will keep working normally. If CLB is stuck in closed state then system will keep injecting with reduced MVAR. . | 2 | Wear-out due to extensive use. Excessive humidity. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | Failure will be detected by firmware by verifying the CARD_HEALTHY feedback (High when power fails). | 2 | 4 | CLB03? | CLB Card Unhealthy | [9 empty] | 5579
SV104-11072 |  |  |  | Resistor fails-short and then fault occurs that engages CLB. | No immediate till the shorted duration. Resistor will fail-open due to over-current. Gate driver PWM path will be broken. No output available at HV transformer board. | If CLB is open, power failure occur and system is in injection and due to iiSC fault now faulty MVAR cannot be bypassed so system will transit to monitoring mode. System cannot go to injection anymore until the fault is cleared. | System will lose injection capability until the MVAR fault is cleared. | 4 | Wear-out due to extensive use. Excessive humidity. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 4 | HALT. Electrical Stress Testing. Thermal Stress Testing. | Failure will be detected by firmware by verifying the CARD_HEALTHY feedback (High when power fails). | 2 | 8 | CLB03? | CLB Card Unhealthy | [9 empty] | 11072
| Full Bridge Circuit | [26 empty] | 0
SV104 - 5580 | Half Bridge Gate Driver IC. | U2, U3 | To provide gate driver signal for half bridge MOSFETs. | Both output are permanently low. | One half bridge section will not have output. Output of Full Bridge circuit will be 12 V at no load. HV transformer board will have no output as soon as load is applied. | On Power failure CLB will retain its state. If particular MVAR is in injection and then power failure of its CLB occurs then it will not effect operation and system will remain in injection. If particular MVAR is bypassed its CLB is closed and system is injecting with reduced MVAR and then power failure occurs on closed CLB then system will retain its state and keeps injecting with reduced MVAR. | System will keep working normally. If CLB is stuck in closed state then system will keep injecting with reduced MVAR. . | 2 | Electrical Overstress (Overvoltage). ESD. Counterfeit part. Stress or impact during assembly. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | Failure will be detected by firmware by verifying the CARD_HEALTHY feedback (High when power fails). | 2 | 4 | CLB03? | CLB Card Unhealthy | [9 empty] | 5580
SV104-11073 |  |  |  | Both output are permanently low and then fault occurs that engages CLB. | One half bridge section will not have output. Output of Full Bridge circuit will be 12 V at no load. HV transformer board will have no output as soon as load is applied. | If CLB is open, power failure occur and system is in injection and due to iiSC fault now faulty MVAR cannot be bypassed so system will transit to monitoring mode. System cannot go to injection anymore until the fault is cleared. | System will lose injection capability until the MVAR fault is cleared. | 4 | Electrical Overstress (Overvoltage). ESD. Counterfeit part. Stress or impact during assembly. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 4 | HALT. Electrical Stress Testing. Thermal Stress Testing. | Failure will be detected by firmware by verifying the CARD_HEALTHY feedback (High when power fails). | 2 | 8 | CLB03? | CLB Card Unhealthy | [9 empty] | 11073
SV104 - 5581 |  |  |  | High side output is permanently low | Full bridge functionality will be disturbed. No output will be available at HV transformer board as soon as load is applied. | On Power failure CLB will retain its state. If particular MVAR is in injection and then power failure of its CLB occurs then it will not effect operation and system will remain in injection. If particular MVAR is bypassed its CLB is closed and system is injecting with reduced MVAR and then power failure occurs on closed CLB then system will retain its state and keeps injecting with reduced MVAR. | System will keep working normally. If CLB is stuck in closed state then system will keep injecting with reduced MVAR. . | 2 | Electrical Overstress (Overvoltage). ESD. Counterfeit part. Stress or impact during assembly. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | Failure will be detected by firmware by verifying the CARD_HEALTHY feedback (High when power fails). | 2 | 4 | CLB03? | CLB Card Unhealthy | [9 empty] | 5581
SV104-11074 |  |  |  | High side output is permanently low and then fault occurs that engages CLB. | Full bridge functionality will be disturbed. No output will be available at HV transformer board as soon as load is applied. | If CLB is open, power failure occur and system is in injection and due to iiSC fault now faulty MVAR cannot be bypassed so system will transit to monitoring mode. System cannot go to injection anymore until the fault is cleared. | System will lose injection capability until the MVAR fault is cleared. | 4 | Electrical Overstress (Overvoltage). ESD. Counterfeit part. Stress or impact during assembly. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 4 | HALT. Electrical Stress Testing. Thermal Stress Testing. | Failure will be detected by firmware by verifying the CARD_HEALTHY feedback (High when power fails). | 2 | 8 | CLB03? | CLB Card Unhealthy | [7 empty] | 0 |  | 11074
SV104 - 5582 |  |  |  | High side output is permanently high | One MOSFET will be permanently turned ON. During times, when low side MOSFET of same half bridge will turn ON, HV DC line get shorted will ground. Due to high current flow, power MOSFETs may get damaged. Input side fuse will burn out and prevent cascading failures. | On Power failure CLB will retain its state. If particular MVAR is in injection and then power failure of its CLB occurs then it will not effect operation and system will remain in injection. If particular MVAR is bypassed its CLB is closed and system is injecting with reduced MVAR and then power failure occurs on closed CLB then system will retain its state and keeps injecting with reduced MVAR. | System will keep working normally. If CLB is stuck in closed state then system will keep injecting with reduced MVAR. . | 2 | Electrical Overstress (Overvoltage). ESD. Counterfeit part. Stress or impact during assembly. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | Failure will be detected by firmware by verifying the CARD_HEALTHY feedback (High when power fails). | 2 | 4 | CLB03? | CLB Card Unhealthy | [9 empty] | 5582
SV104-11075 |  |  |  | High side output is permanently high and then fault occurs that engages CLB. | One MOSFET will be permanently turned ON. During times, when low side MOSFET of same half bridge will turn ON, HV DC line get shorted will ground. Due to high current flow, power MOSFETs may get damaged. Input side fuse will burn out and prevent cascading failures. | If CLB is open, power failure occur and system is in injection and due to iiSC fault now faulty MVAR cannot be bypassed so system will transit to monitoring mode. System cannot go to injection anymore until the fault is cleared. | System will lose injection capability until the MVAR fault is cleared. | 4 | Electrical Overstress (Overvoltage). ESD. Counterfeit part. Stress or impact during assembly. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 4 | HALT. Electrical Stress Testing. Thermal Stress Testing. | Failure will be detected by firmware by verifying the CARD_HEALTHY feedback (High when power fails). | 2 | 8 | CLB03? | CLB Card Unhealthy | [9 empty] | 11075
SV104 - 8908 | Half Bridge Gate Driver IC. | U2, U3 | To provide gate driver signal for half bridge MOSFETs. | Low side output is permanently low | Full bridge functionality will be disturbed. No output will be available at HV transformer board as soon as load is applied. | On Power failure CLB will retain its state. If particular MVAR is in injection and then power failure of its CLB occurs then it will not effect operation and system will remain in injection. If particular MVAR is bypassed its CLB is closed and system is injecting with reduced MVAR and then power failure occurs on closed CLB then system will retain its state and keeps injecting with reduced MVAR. | System will keep working normally. If CLB is stuck in closed state then system will keep injecting with reduced MVAR. . | 2 | Electrical Overstress (Overvoltage). ESD. Counterfeit part. Stress or impact during assembly. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | Failure will be detected by firmware by verifying the CARD_HEALTHY feedback (High when power fails). | 2 | 4 | CLB03? | CLB Card Unhealthy | [9 empty] | 8908
SV104-11076 |  |  |  | Low side output is permanently low and then fault occurs that engages CLB. | Full bridge functionality will be disturbed. No output will be available at HV transformer board as soon as load is applied. | If CLB is open, power failure occur and system is in injection and due to iiSC fault now faulty MVAR cannot be bypassed so system will transit to monitoring mode. System cannot go to injection anymore until the fault is cleared. | System will lose injection capability until the MVAR fault is cleared. | 4 | Electrical Overstress (Overvoltage). ESD. Counterfeit part. Stress or impact during assembly. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 4 | HALT. Electrical Stress Testing. Thermal Stress Testing. | Failure will be detected by firmware by verifying the CARD_HEALTHY feedback (High when power fails). | 2 | 8 | CLB03? | CLB Card Unhealthy | [9 empty] | 11076
SV104 - 8909 |  |  |  | Low side output is permanently high. | During times, when high side MOSFET of same half bridge will turn ON, HV DC line get shorted with ground. Due to high current flow, power MOSFETs may get damaged. Input side fuse will burn out and prevent cascading failures. | On Power failure CLB will retain its state. If particular MVAR is in injection and then power failure of its CLB occurs then it will not effect operation and system will remain in injection. If particular MVAR is bypassed its CLB is closed and system is injecting with reduced MVAR and then power failure occurs on closed CLB then system will retain its state and keeps injecting with reduced MVAR. | System will keep working normally. If CLB is stuck in closed state then system will keep injecting with reduced MVAR. . | 2 | Electrical Overstress (Overvoltage). ESD. Counterfeit part. Stress or impact during assembly. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | Failure will be detected by firmware by verifying the CARD_HEALTHY feedback (High when power fails). | 2 | 4 | CLB03? | CLB Card Unhealthy | [9 empty] | 8909
SV104-11077 |  |  |  | Low side output is permanently high. and then fault occurs that engages CLB. | During times, when high side MOSFET of same half bridge will turn ON, HV DC line get shorted with ground. Due to high current flow, power MOSFETs may get damaged. Input side fuse will burn out and prevent cascading failures. | If CLB is open, power failure occur and system is in injection and due to iiSC fault now faulty MVAR cannot be bypassed so system will transit to monitoring mode. System cannot go to injection anymore until the fault is cleared. | System will lose injection capability until the MVAR fault is cleared. | 4 | Electrical Overstress (Overvoltage). ESD. Counterfeit part. Stress or impact during assembly. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 4 | HALT. Electrical Stress Testing. Thermal Stress Testing. | Failure will be detected by firmware by verifying the CARD_HEALTHY feedback (High when power fails). | 2 | 8 | CLB03? | CLB Card Unhealthy | [9 empty] | 11077
SV104 - 8910 |  |  |  | Both outputs are permanently high | Both MOSFETs will be permanently turned ON. HV DC line will get shorted with ground. Due to high current flow, power MOSFETs may get damaged. Input side fuse will burn out and prevent cascading failures. | On Power failure CLB will retain its state. If particular MVAR is in injection and then power failure of its CLB occurs then it will not effect operation and system will remain in injection. If particular MVAR is bypassed its CLB is closed and system is injecting with reduced MVAR and then power failure occurs on closed CLB then system will retain its state and keeps injecting with reduced MVAR. | System will keep working normally. If CLB is stuck in closed state then system will keep injecting with reduced MVAR. . | 2 | Electrical Overstress (Overvoltage). ESD. Counterfeit part. Stress or impact during assembly. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | Failure will be detected by firmware by verifying the CARD_HEALTHY feedback (High when power fails). | 2 | 4 | CLB03? | CLB Card Unhealthy | [9 empty] | 8910
SV104-11078 |  |  |  | Both outputs are permanently high and then fault occurs that engages CLB. | Both MOSFETs will be permanently turned ON. HV DC line will get shorted with ground. Due to high current flow, power MOSFETs may get damaged. Input side fuse will burn out and prevent cascading failures. | If CLB is open, power failure occur and system is in injection and due to iiSC fault now faulty MVAR cannot be bypassed so system will transit to monitoring mode. System cannot go to injection anymore until the fault is cleared. | System will lose injection capability until the MVAR fault is cleared. | 4 | Electrical Overstress (Overvoltage). ESD. Counterfeit part. Stress or impact during assembly. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 4 | HALT. Electrical Stress Testing. Thermal Stress Testing. | Failure will be detected by firmware by verifying the CARD_HEALTHY feedback (High when power fails). | 2 | 8 | CLB03? | CLB Card Unhealthy | [9 empty] | 11078
SV104 - 5583 | Half Bridge Gate Driver IC - Filter Capacitor. | C4,C5 | To suppress ripples and to provide decoupling | Capacitor fails-open | Output of gate driver IC will be affected. No output available at HV transformer board. | On Power failure CLB will retain its state. If particular MVAR is in injection and then power failure of its CLB occurs then it will not effect operation and system will remain in injection. If particular MVAR is bypassed its CLB is closed and system is injecting with reduced MVAR and then power failure occurs on closed CLB then system will retain its state and keeps injecting with reduced MVAR. | System will keep working normally. If CLB is stuck in closed state then system will keep injecting with reduced MVAR. . | 2 | Mechanical stress. Localized heating for long time will separate end connection of capacitor. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | Failure will be detected by firmware by verifying the CARD_HEALTHY feedback (High when power fails). | 2 | 4 | CLB03? | CLB Card Unhealthy | [9 empty] | 5583
SV104-11079 |  |  |  | Capacitor fails-open and then fault occurs that engages CLB. | Output of gate driver IC will be affected. No output available at HV transformer board. | If CLB is open, power failure occur and system is in injection and due to iiSC fault now faulty MVAR cannot be bypassed so system will transit to monitoring mode. System cannot go to injection anymore until the fault is cleared. | System will lose injection capability until the MVAR fault is cleared. | 4 | Mechanical stress. Localized heating for long time will separate end connection of capacitor. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 4 | HALT. Electrical Stress Testing. Thermal Stress Testing. | Failure will be detected by firmware by verifying the CARD_HEALTHY feedback (High when power fails). | 2 | 8 | CLB03? | CLB Card Unhealthy | [9 empty] | 11079
SV104 - 5584 |  |  |  | Capacitor fails-short | Output of gate driver IC will be affected. No output available at HV transformer board. | On Power failure CLB will retain its state. If particular MVAR is in injection and then power failure of its CLB occurs then it will not effect operation and system will remain in injection. If particular MVAR is bypassed its CLB is closed and system is injecting with reduced MVAR and then power failure occurs on closed CLB then system will retain its state and keeps injecting with reduced MVAR. | System will keep working normally. If CLB is stuck in closed state then system will keep injecting with reduced MVAR. . | 2 | Wear-out due to dielectric degradation. High-voltage transients. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | Failure will be detected by firmware by verifying the CARD_HEALTHY feedback (High when power fails). | 2 | 4 | CLB03? | CLB Card Unhealthy | [7 empty] | 0 |  | 5584
SV104-11080 |  |  |  | Capacitor fails-short and then fault occurs that engages CLB. | Output of gate driver IC will be affected. No output available at HV transformer board. | If CLB is open, power failure occur and system is in injection and due to iiSC fault now faulty MVAR cannot be bypassed so system will transit to monitoring mode. System cannot go to injection anymore until the fault is cleared. | System will lose injection capability until the MVAR fault is cleared. | 4 | Wear-out due to dielectric degradation. High-voltage transients. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 4 | HALT. Electrical Stress Testing. Thermal Stress Testing. | Failure will be detected by firmware by verifying the CARD_HEALTHY feedback (High when power fails). | 2 | 8 | CLB03? | CLB Card Unhealthy | [9 empty] | 11080
SV104 - 5585 | Gate Driver Output Circuit - Resistor. | R7,R24,R6,R23 | To provide path between gate driver IC and gate. | Resistor fails-open. | Output path of gate driver IC will be broken for one MOSFET. Distorted square wave will be available at full bridge circuit output. HV transformer board will have lesser output than desired. | If no other failure is observed on the board, CLB driver board will stay powered. Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | Over voltage. Over Temperature. Over stress due to shock or vibration. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [11 empty] | 5585
SV104 - 5586 |  |  |  | Resistor fails-short. | Over-current will cause the resistor to eventually fail-open. Output path of gate driver IC will be broken for one MOSFET. Distorted square wave will be available at full bridge circuit output. HV transformer board will have lesser output than desired. | If no other failure is observed on the board, CLB driver board will stay powered. Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | Wear-out due to extensive use. Excessive humidity. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [11 empty] | 5586
SV104 - 5587 | Gate Driver Output Circuit - General Purpose Diode. | D1,D2,D3,D4 | To turn off the MOSFET quickly through low resistance path at gate. | Diode fails-open. | MOSFET will turn off through larger resistor which will result in increased switching losses. No immediate effect in case of normal operations. | If no other failure is observed on the board, CLB driver board will stay powered. Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | Excessive forward current flow. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [11 empty] | 5587
SV104 - 5588 |  |  |  | Diode fail-short. | Over-current will cause the diode to eventually fail-open. MOSFET will turn off through larger resistor which will result in increased switching losses. No immediate effect in case of normal operations. | If no other failure is observed on the board, CLB driver board will stay powered. Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | Large reverse voltage. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [11 empty] | 5588
SV104-11081 | Gate Driver Output Circuit -Discharge Resistor. | R2,R3,R20,R21 | To provide low resistance path between gate driver IC and gate to discharge gate capacitance. | Resistor fails-open. | Gate Capacitance will discharge slowly through high resistance path thus on/off time will be disturbed Switching losses will increase. No immediate effect ion board. | If no other failure is observed on the board, CLB driver board will stay powered. Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | Over voltage. Over Temperature. Over stress due to shock or vibration. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [11 empty] | 11081
SV104-11082 |  |  |  | Resistor fails-short. | Switching losses will increase. No immediate effect on board. | If no other failure is observed on the board, CLB driver board will stay powered. Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | Wear-out due to extensive use. Excessive humidity. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [11 empty] | 11082
SV104-11083 | MOSFET resistance for Miller Capacitance | R10,R27,R11,R26 | To discharge capacitance between all terminals of MOSFET | Resistor fails-open | Abnormal Behavior of MOSFET Might turn ON/OFF abnormally and can damage board. No output available at HV transformer board | On Power failure CLB will retain its state. If particular MVAR is in injection and then power failure of its CLB occurs then it will not effect operation and system will remain in injection. If particular MVAR is bypassed its CLB is closed and system is injecting with reduced MVAR and then power failure occurs on closed CLB then system will retain its state and keeps injecting with reduced MVAR. | System will keep working normally. If CLB is stuck in closed state then system will keep injecting with reduced MVAR. . | 2 | Over voltage. Over Temperature. Over stress due to shock or vibration. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. Vibration testing. | None. | 5 | 10 | [9 empty] | 0 |  | 11083
SV104-11084 |  |  |  | resistor fails-open and then fault occurs that engages CLB. | Abnormal Behavior of MOSFET Might turn ON/OFF abnormally. Once Board Reboots no output will be available No output available at HV transformer board | If CLB is open, power failure occur and system is in injection and due to iiSC fault now faulty MVAR cannot be bypassed so system will transit to monitoring mode. System cannot go to injection anymore until the fault is cleared. | System will lose injection capability until the MVAR fault is cleared. | 4 | Over voltage. Over Temperature. Over stress due to shock or vibration. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 4 | HALT. Electrical Stress Testing. Thermal Stress Testing. Vibration testing. | Failure will be detected by firmware by verifying the CARD_HEALTHY feedback (High when power fails). | 2 | 8 | CLB03? | CLB Card Unhealthy | [9 empty] | 11084
SV104-11085 |  |  |  | Resistor fails-short | Gate and Source of MOSFET will have no voltage difference so MOSFET cannot operate No output available at HV transformer board | On Power failure CLB will retain its state. If particular MVAR is in injection and then power failure of its CLB occurs then it will not effect operation and system will remain in injection. If particular MVAR is bypassed its CLB is closed and system is injecting with reduced MVAR and then power failure occurs on closed CLB then system will retain its state and keeps injecting with reduced MVAR. | System will keep working normally. If CLB is stuck in closed state then system will keep injecting with reduced MVAR. . | 2 | Wear-out due to extensive use. Excessive humidity. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. Vibration testing. | None. | 5 | 10 | CLB03? | CLB Card Unhealthy | [9 empty] | 11085
SV104-11086 |  |  |  | resistor fails-short and then fault occurs that engages CLB. | Gate and Source of MOSFET will have no voltage difference so MOSFET cannot operate No output available at HV transformer board | If CLB is open, power failure occur and system is in injection and due to iiSC fault now faulty MVAR cannot be bypassed so system will transit to monitoring mode. System cannot go to injection anymore until the fault is cleared. | System will lose injection capability until the MVAR fault is cleared. | 4 | Wear-out due to extensive use. Excessive humidity. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 4 | HALT. Electrical Stress Testing. Thermal Stress Testing. Vibration testing. | Failure will be detected by firmware by verifying the CARD_HEALTHY feedback (High when power fails). | 2 | 8 | CLB03? | CLB Card Unhealthy | [9 empty] | 11086
SV104-11087 | Half Bridge Gate Driver IC - High Side Supply Capacitor. | C7,C15,C16,C8 | To provide high side supply and to ensure bootstrapping in order to operate MOSFET. | One Capacitor fails-open. | No immediate effect as the parallel capacitor will be available and will make sure that MOSFET works properly | If no other failure is observed on the board, CLB driver board will stay powered. Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | Mechanical stress. Localized heating for long time will separate end connection of capacitor. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [11 empty] | 11087
SV104-11088 |  |  |  | Both Capacitors fails-open. | MOSFET Cannot operate properly No output available at HV transformer board | On Power failure CLB will retain its state. If particular MVAR is in injection and then power failure of its CLB occurs then it will not effect operation and system will remain in injection. If particular MVAR is bypassed its CLB is closed and system is injecting with reduced MVAR and then power failure occurs on closed CLB then system will retain its state and keeps injecting with reduced MVAR. | System will keep working normally. If CLB is stuck in closed state then system will keep injecting with reduced MVAR. . | 2 | Mechanical stress. Localized heating for long time will separate end connection of capacitor. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 10 | CLB03? | CLB Card Unhealthy | [9 empty] | 11088
SV104-11089 |  |  |  | Capacitor fails-open and then fault occurs that engages CLB. | MOSFET Cannot operate properly No output available at HV transformer board | If CLB is open, power failure occur and system is in injection and due to iiSC fault now faulty MVAR cannot be bypassed so system will transit to monitoring mode. System cannot go to injection anymore until the fault is cleared. | System will lose injection capability until the MVAR fault is cleared. | 4 | Mechanical stress. Localized heating for long time will separate end connection of capacitor. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 4 | HALT. Electrical Stress Testing. Thermal Stress Testing. Vibration testing. | Failure will be detected by firmware by verifying the CARD_HEALTHY feedback (High when power fails). | 2 | 8 | CLB03? | CLB Card Unhealthy | [7 empty] | 0 |  | 11089
SV104-11090 |  |  |  | Capacitor fails-short. | MOSFET Cannot operate properly IC may get damaged No output available at HV transformer board | On Power failure CLB will retain its state. If particular MVAR is in injection and then power failure of its CLB occurs then it will not effect operation and system will remain in injection. If particular MVAR is bypassed its CLB is closed and system is injecting with reduced MVAR and then power failure occurs on closed CLB then system will retain its state and keeps injecting with reduced MVAR. | System will keep working normally. If CLB is stuck in closed state then system will keep injecting with reduced MVAR. . | 2 | Wear-out due to dielectric degradation. High-voltage transients. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 10 | CLB03? | CLB Card Unhealthy | [9 empty] | 11090
SV104-11091 |  |  |  | Capacitor fails-short and then fault occurs that engages CLB. | MOSFET Cannot operate properly IC may get damaged No output available at HV transformer board | If CLB is open, power failure occur and system is in injection and due to iiSC fault now faulty MVAR cannot be bypassed so system will transit to monitoring mode. System cannot go to injection anymore until the fault is cleared. | System will lose injection capability until the MVAR fault is cleared. | 4 | Wear-out due to dielectric degradation. High-voltage transients. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 4 | HALT. Electrical Stress Testing. Thermal Stress Testing. Vibration testing. | Failure will be detected by firmware by verifying the CARD_HEALTHY feedback (High when power fails). | 2 | 8 | CLB03? | CLB Card Unhealthy | [9 empty] | 11091
SV104 - 5589 | Full Bridge Circuit - MOSFET | Q1,Q2,Q3,Q4 | To convert HV DC to HV AC signal. | MOSFET fails-open. | Distorted square wave will be available at full bridge circuit output. HV transformer board will have lesser output than desired. | If no other failure is observed on the board, CLB driver board will stay powered. Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | Overheating Mechanical stress resulting in cracked MOSFET body. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [11 empty] | 5589
SV104 - 5590 |  |  |  | MOSFET fails-short | No voltage will be available at transformer output, for the shorted duration. No output available at HV transformer board. | On Power failure CLB will retain its state. If particular MVAR is in injection and then power failure of its CLB occurs then it will not effect operation and system will remain in injection. If particular MVAR is bypassed its CLB is closed and system is injecting with reduced MVAR and then power failure occurs on closed CLB then system will retain its state and keeps injecting with reduced MVAR. | System will keep working normally. If CLB is stuck in closed state then system will keep injecting with reduced MVAR. . | 2 | Transients Overheating as a result of loose connection with heat sink Overcurrent Counterfeit part Damage during mechanical assembly of board Metallic debris stuck in between terminals | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | Failure will be detected by firmware by verifying the CARD_HEALTHY feedback (High when power fails). | 2 | 4 | CLB03? | CLB Card Unhealthy | [7 empty] | 0 |  | 5590
SV104-11092 |  |  |  | MOSFET fails-short and then fault occurs that engages CLB. | No voltage will be available at transformer output, for the shorted duration. No output available at HV transformer board. | If CLB is open, power failure occur and system is in injection and due to iiSC fault now faulty MVAR cannot be bypassed so system will transit to monitoring mode. System cannot go to injection anymore until the fault is cleared. | System will lose injection capability until the MVAR fault is cleared. | 4 | Transients Overheating as a result of loose connection with heat sink Overcurrent Counterfeit part Damage during mechanical assembly of board Metallic debris stuck in between terminals | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 4 | HALT. Electrical Stress Testing. Thermal Stress Testing. | Failure will be detected by firmware by verifying the CARD_HEALTHY feedback (High when power fails). | 2 | 8 | CLB03? | CLB Card Unhealthy | [9 empty] | 11092
SV104-11093 | Gate Driver Output Circuit -Pull Down resistance. | R29,R8 | To provide current sense signal to controller | One Resistor fails-open. | Current over limit value will decrease down to half. No immediate affect in normal condition but in case of overloaded condition current limit will be activated early. | If no other failure is observed on the board, CLB driver board will stay powered. Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | Over voltage. Over Temperature. Over stress due to shock or vibration. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [11 empty] | 11093
SV104-11094 |  |  |  | Both Resistor fails-open. | Full bridge circuit ground connection will be disconnected No output available at HV transformer board | On Power failure CLB will retain its state. If particular MVAR is in injection and then power failure of its CLB occurs then it will not effect operation and system will remain in injection. If particular MVAR is bypassed its CLB is closed and system is injecting with reduced MVAR and then power failure occurs on closed CLB then system will retain its state and keeps injecting with reduced MVAR. | System will keep working normally. If CLB is stuck in closed state then system will keep injecting with reduced MVAR. . | 2 | Over voltage. Over Temperature. Over stress due to shock or vibration. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 10 | CLB03? | CLB Card Unhealthy | [9 empty] | 11094
SV104-11095 |  |  |  | Both resistors fail open and then fault occurs that engages CLB. | Full bridge circuit ground connection will be disconnected No output available at HV transformer board | If CLB is open, power failure occur and system is in injection and due to iiSC fault now faulty MVAR cannot be bypassed so system will transit to monitoring mode. System cannot go to injection anymore until the fault is cleared. | System will lose injection capability until the MVAR fault is cleared. | 4 | Over voltage. Over Temperature. Over stress due to shock or vibration. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 4 | HALT. Electrical Stress Testing. Thermal Stress Testing. | Failure will be detected by firmware by verifying the CARD_HEALTHY feedback (High when power fails). | 2 | 8 | CLB03? | CLB Card Unhealthy | [7 empty] | 0 |  | 11095
SV104-11096 |  |  |  | Resistor fails-short. | No immediate effect in case of normal operations. In case of any fault, overcurrent protection will not be available. | If no other failure is observed on the board, CLB driver board will stay powered. Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | Wear-out due to extensive use. Excessive humidity. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [11 empty] | 11096
SV104 - 5591 | HV Isolation Transformer | P113720 | To step down 400 V AC to 24 V AC. | Primary winding fails-open | No voltage will be available at transformer output. No output available at HV transformer board. | On Power failure CLB will retain its state. If particular MVAR is in injection and then power failure of its CLB occurs then it will not effect operation and system will remain in injection. If particular MVAR is bypassed its CLB is closed and system is injecting with reduced MVAR and then power failure occurs on closed CLB then system will retain its state and keeps injecting with reduced MVAR. | System will keep working normally. If CLB is stuck in closed state then system will keep injecting with reduced MVAR. . | 2 | High operating temperature. Overloading. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | Failure will be detected by firmware by verifying the CARD_HEALTHY feedback (High when power fails). | 2 | 4 | CLB03? | CLB Card Unhealthy | [9 empty] | 5591
SV104-11097 |  |  |  | Primary winding fails-open and then fault occurs that engages CLB. | No voltage will be available at transformer output. No output available at HV transformer board. | If CLB is open, power failure occur and system is in injection and due to iiSC fault now faulty MVAR cannot be bypassed so system will transit to monitoring mode. System cannot go to injection anymore until the fault is cleared. | System will lose injection capability until the MVAR fault is cleared. | 4 | High operating temperature. Overloading. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 4 | HALT. Electrical Stress Testing. Thermal Stress Testing. | Failure will be detected by firmware by verifying the CARD_HEALTHY feedback (High when power fails). | 2 | 8 | CLB03? | CLB Card Unhealthy | [7 empty] | 0 |  | 11097
SV104 - 5592 |  |  |  | Secondary winding fails-open | No output will be available at HV transformer board. | On Power failure CLB will retain its state. If particular MVAR is in injection and then power failure of its CLB occurs then it will not effect operation and system will remain in injection. If particular MVAR is bypassed its CLB is closed and system is injecting with reduced MVAR and then power failure occurs on closed CLB then system will retain its state and keeps injecting with reduced MVAR. | System will keep working normally. If CLB is stuck in closed state then system will keep injecting with reduced MVAR. . | 2 | High operating temperature. Overloading. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | Failure will be detected by firmware by verifying the CARD_HEALTHY feedback (High when power fails). | 2 | 4 | CLB03? | CLB Card Unhealthy | [9 empty] | 5592
SV104-11098 |  |  |  | Secondary winding fails-open and then fault occurs that engages CLB. | No output will be available at HV transformer board. | If CLB is open, power failure occur and system is in injection and due to iiSC fault now faulty MVAR cannot be bypassed so system will transit to monitoring mode. System cannot go to injection anymore until the fault is cleared. | System will lose injection capability until the MVAR fault is cleared. | 4 | High operating temperature. Overloading. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 4 | HALT. Electrical Stress Testing. Thermal Stress Testing. | Failure will be detected by firmware by verifying the CARD_HEALTHY feedback (High when power fails). | 2 | 8 | CLB03? | CLB Card Unhealthy | [9 empty] | 11098
SV104 - 5593 |  |  |  | Core degradation. | Output voltage will be less than desired value. | If no other failure is observed on the board, CLB driver board will stay powered. Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | Mechanical Stress | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [11 empty] | 5593
SV104 - 5594 |  |  |  | Winding insulation melting. | Turn ratio of transformer will be affected. Output voltage will be less than desired value. | If no other failure is observed on the board, CLB driver board will stay powered. Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | Over voltage. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [11 empty] | 5594
SV104 - 6985 |  |  |  | Isolation Failure | If failure is such that board cannot provide any level of isolation then it will damage CLB driver board driver board. | On Power failure CLB will retain its state. If particular MVAR is in injection and then power failure of its CLB occurs then it will not effect operation and system will remain in injection. If particular MVAR is bypassed its CLB is closed and system is injecting with reduced MVAR and then power failure occurs on closed CLB then system will retain its state and keeps injecting with reduced MVAR. | System will keep working normally. If CLB is stuck in closed state then system will keep injecting with reduced MVAR. . | 2 | Temperature cycling. Manufacturing Deficiency. Vibration. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | Failure will be detected by firmware by verifying the CARD_HEALTHY feedback (High when power fails). | 2 | 4 | CLB03? | CLB Card Unhealthy | [9 empty] | 6985
SV104-11099 |  |  |  | Isolation Failure and then fault occurs that engages CLB. | If failure is such that board cannot provide any level of isolation then it will damage CLB driver board driver board. | If CLB is open, power failure occur and system is in injection and due to iiSC fault now faulty MVAR cannot be bypassed so system will transit to monitoring mode. System cannot go to injection anymore until the fault is cleared. | System will lose injection capability until the MVAR fault is cleared. | 4 | Temperature cycling. Manufacturing Deficiency. Vibration. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 4 | HALT. Electrical Stress Testing. Thermal Stress Testing. | Failure will be detected by firmware by verifying the CARD_HEALTHY feedback (High when power fails). | 2 | 8 | CLB03? | CLB Card Unhealthy | [7 empty] | 0 |  | 11099
SV104 - 6986 |  |  |  | Auxiliary winding failure(Open) | No auxiliary voltage will be available. Startup circuit will not shutdown eventually burning out. No output will be available for HV-ISO board | On Power failure CLB will retain its state. If particular MVAR is in injection and then power failure of its CLB occurs then it will not effect operation and system will remain in injection. If particular MVAR is bypassed its CLB is closed and system is injecting with reduced MVAR and then power failure occurs on closed CLB then system will retain its state and keeps injecting with reduced MVAR. | System will keep working normally. If CLB is stuck in closed state then system will keep injecting with reduced MVAR. . | 2 | Over voltage. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | Failure will be detected by firmware by verifying the CARD_HEALTHY feedback (High when power fails). | 2 | 4 | CLB03? | CLB Card Unhealthy | [9 empty] | 6986
SV104-11100 |  |  |  | Auxiliary winding failure(Open) and then fault occurs that engages CLB. | No auxiliary voltage will be available. Startup circuit will not shutdown eventually burning out. No output will be available for HV-ISO board | If CLB is open, power failure occur and system is in injection and due to iiSC fault now faulty MVAR cannot be bypassed so system will transit to monitoring mode. System cannot go to injection anymore until the fault is cleared. | System will lose injection capability until the MVAR fault is cleared. | 4 | Over voltage. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 4 | HALT. Electrical Stress Testing. Thermal Stress Testing. | Failure will be detected by firmware by verifying the CARD_HEALTHY feedback (High when power fails). | 2 | 8 | CLB03? | CLB Card Unhealthy | [9 empty] | 11100
SV104 - 6987 |  |  |  | Post insulator fails | If failure is such that board cannot provide any level of isolation then it will damage CLB driver board. | On Power failure CLB will retain its state. If particular MVAR is in injection and then power failure of its CLB occurs then it will not effect operation and system will remain in injection. If particular MVAR is bypassed its CLB is closed and system is injecting with reduced MVAR and then power failure occurs on closed CLB then system will retain its state and keeps injecting with reduced MVAR. | System will keep working normally. If CLB is stuck in closed state then system will keep injecting with reduced MVAR. . | 2 | Corrosion. Manufacturing Deficiency. Vibration. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | Failure will be detected by firmware by verifying the CARD_HEALTHY feedback (High when power fails). | 2 | 4 | CLB03? | CLB Card Unhealthy | [9 empty] | 6987
SV104-11101 |  |  |  | Post insulator fails and then fault occurs that engages CLB. | If failure is such that board cannot provide any level of isolation then it will damage CLB driver board. | If CLB is open, power failure occur and system is in injection and due to iiSC fault now faulty MVAR cannot be bypassed so system will transit to monitoring mode. System cannot go to injection anymore until the fault is cleared. | System will lose injection capability until the MVAR fault is cleared. | 4 | Corrosion. Manufacturing Deficiency. Vibration. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 4 | HALT. Electrical Stress Testing. Thermal Stress Testing. | Failure will be detected by firmware by verifying the CARD_HEALTHY feedback (High when power fails). | 2 | 8 | CLB03? | CLB Card Unhealthy | [9 empty] | 11101
SV104 - 6988 |  |  |  | Potting crack or physical damage | Partial discharge will start resulting in degradation of isolation barrier with the time. Eventually degradation will reach to a level where failure will occur and CLB driver board will get damaged. | On Power failure CLB will retain its state. If particular MVAR is in injection and then power failure of its CLB occurs then it will not effect operation and system will remain in injection. If particular MVAR is bypassed its CLB is closed and system is injecting with reduced MVAR and then power failure occurs on closed CLB then system will retain its state and keeps injecting with reduced MVAR. | System will keep working normally. If CLB is stuck in closed state then system will keep injecting with reduced MVAR. . | 2 | Corrosion. Manufacturing Deficiency. Vibration. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | Failure will be detected by firmware by verifying the CARD_HEALTHY feedback (High when power fails). | 2 | 4 | CLB03? | CLB Card Unhealthy | [7 empty] | 0 |  | 6988
SV104-11102 |  |  |  | Potting crack or physical damage and then fault occurs that engages CLB. | Partial discharge will start resulting in degradation of isolation barrier with the time. Eventually degradation will reach to a level where failure will occur and CLB driver board will get damaged. | If CLB is open, power failure occur and system is in injection and due to iiSC fault now faulty MVAR cannot be bypassed so system will transit to monitoring mode. System cannot go to injection anymore until the fault is cleared. | System will lose injection capability until the MVAR fault is cleared. | 4 | Corrosion. Manufacturing Deficiency. Vibration. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 4 | HALT. Electrical Stress Testing. Thermal Stress Testing. | Failure will be detected by firmware by verifying the CARD_HEALTHY feedback (High when power fails). | 2 | 8 | CLB03? | CLB Card Unhealthy | [9 empty] | 11102
SV104 - 5595 | HV Isolation Transformer - output Side Full Rectifier - Diode | D5,D6,D8 | To convert 24 V AC to 24 V DC. | Diode fails-open | Output cut to half if half side is working. . | On Power failure CLB will retain its state. If particular MVAR is in injection and then power failure of its CLB occurs then it will not effect operation and system will remain in injection. If particular MVAR is bypassed its CLB is closed and system is injecting with reduced MVAR and then power failure occurs on closed CLB then system will retain its state and keeps injecting with reduced MVAR. | System will keep working normally. If CLB is stuck in closed state then system will keep injecting with reduced MVAR. . | 2 | Excessive forward current flow. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | Failure will be detected by firmware by verifying the CARD_HEALTHY feedback (High when power fails). | 2 | 4 | CLB03? | CLB Card Unhealthy | [9 empty] | 5595
SV104-11103 |  |  |  | Diode fails-open and then fault occurs that engages CLB. | Output cut to half if half side is working. . | If CLB is open, power failure occur and system is in injection and due to iiSC fault now faulty MVAR cannot be bypassed so system will transit to monitoring mode. System cannot go to injection anymore until the fault is cleared. | System will lose injection capability until the MVAR fault is cleared. | 4 | Excessive forward current flow. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 4 | HALT. Electrical Stress Testing. Thermal Stress Testing. | Failure will be detected by firmware by verifying the CARD_HEALTHY feedback (High when power fails). | 2 | 8 | CLB03? | CLB Card Unhealthy | [9 empty] | 11103
SV104 - 5596 |  |  |  | Diode fails-short | Secondary winding will get shorted if any diode fails-short. As a result of shortage, excessive amount of current will flow damaging two diodes permanently. Diodes will eventually get open and no output will be available | On Power failure CLB will retain its state. If particular MVAR is in injection and then power failure of its CLB occurs then it will not effect operation and system will remain in injection. If particular MVAR is bypassed its CLB is closed and system is injecting with reduced MVAR and then power failure occurs on closed CLB then system will retain its state and keeps injecting with reduced MVAR. | System will keep working normally. If CLB is stuck in closed state then system will keep injecting with reduced MVAR. . | 2 | Large reverse voltage. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | Failure will be detected by firmware by verifying the CARD_HEALTHY feedback (High when power fails). | 2 | 4 | CLB03? | CLB Card Unhealthy | [9 empty] | 5596
SV104-11104 |  |  |  | Diode fails-short and then fault occurs that engages CLB. | Secondary winding will get shorted if any diode fails-short. As a result of shortage, excessive amount of current will flow damaging two diodes permanently. Diodes will eventually get open and no output will be available | If CLB is open, power failure occur and system is in injection and due to iiSC fault now faulty MVAR cannot be bypassed so system will transit to monitoring mode. System cannot go to injection anymore until the fault is cleared. | System will lose injection capability until the MVAR fault is cleared. | 4 | Electrical Overstress (Overvoltage). ESD. Counterfeit part. Stress or impact during assembly. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 4 | HALT. Electrical Stress Testing. Thermal Stress Testing. | Failure will be detected by firmware by verifying the CARD_HEALTHY feedback (High when power fails). | 2 | 8 | CLB03? | CLB Card Unhealthy | [9 empty] | 11104
SV104 - 5229 | Output Side Capacitor. | C13,C14 | To suppress output side ripples and to provide filtration. | Capacitor fails-open. | Output voltage may have ripples. No immediate effect on HV transformer board output. | If no other failure is observed on the board, CLB driver board will stay powered. Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | Mechanical stress. Localized heating for long time will separate end connection of capacitor. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [11 empty] | 5229
SV104 - 5230 |  |  |  | Capacitor fails-short. | No voltage available at the output for the shorted duration. | On Power failure CLB will retain its state. If particular MVAR is in injection and then power failure of its CLB occurs then it will not effect operation and system will remain in injection. If particular MVAR is bypassed its CLB is closed and system is injecting with reduced MVAR and then power failure occurs on closed CLB then system will retain its state and keeps injecting with reduced MVAR. | System will keep working normally. If CLB is stuck in closed state then system will keep injecting with reduced MVAR. . | 2 | Wear-out due to dielectric degradation. High-voltage transients. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | Failure will be detected by firmware by verifying the CARD_HEALTHY feedback (High when power fails). | 2 | 4 | CLB03? | CLB Card Unhealthy | [7 empty] | 0 |  | 5230
SV104-11105 |  |  |  | Capacitor fails-short and then fault occurs that engages CLB. | No voltage available at the output for the shorted duration. Redundant power to iSCR driver board will be cut-off. . | If CLB is open, power failure occur and system is in injection and due to iiSC fault now faulty MVAR cannot be bypassed so system will transit to monitoring mode. System cannot go to injection anymore until the fault is cleared. | System will lose injection capability until the MVAR fault is cleared. | 4 | Wear-out due to dielectric degradation. High-voltage transients. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 4 | HALT. Electrical Stress Testing. Thermal Stress Testing. | Failure will be detected by firmware by verifying the CARD_HEALTHY feedback (High when power fails). | 2 | 8 | CLB03? | CLB Card Unhealthy | [7 empty] | 0 |  | 11105
SV104 - 5597 | HV Isolation Transformer - Feedback Side Full Rectifier - Diode | D15,D16,D19,D20 | To convert 24 V AC to 24 V DC for feedback. | Diode fails-open | Output cut to half if half side is working. | On Power failure CLB will retain its state. If particular MVAR is in injection and then power failure of its CLB occurs then it will not effect operation and system will remain in injection. If particular MVAR is bypassed its CLB is closed and system is injecting with reduced MVAR and then power failure occurs on closed CLB then system will retain its state and keeps injecting with reduced MVAR. | System will keep working normally. If CLB is stuck in closed state then system will keep injecting with reduced MVAR. . | 2 | Excessive forward current flow. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | Failure will be detected by firmware by verifying the CARD_HEALTHY feedback (High when power fails). | 2 | 4 | CLB03? | CLB Card Unhealthy | [9 empty] | 5597
SV104-11106 |  |  |  | Diode fails-open and then fault occurs that engages CLB. | Output cut to half if half side is working. | If CLB is open, power failure occur and system is in injection and due to iiSC fault now faulty MVAR cannot be bypassed so system will transit to monitoring mode. System cannot go to injection anymore until the fault is cleared. | System will lose injection capability until the MVAR fault is cleared. | 4 | Excessive forward current flow. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 4 | HALT. Electrical Stress Testing. Thermal Stress Testing. | Failure will be detected by firmware by verifying the CARD_HEALTHY feedback (High when power fails). | 2 | 8 | CLB03? | CLB Card Unhealthy | [9 empty] | 11106
SV104 - 5598 |  |  |  | Diode fails-short | Auxiliary winding will get shorted if any diode fails-short. As a result of shortage, excessive amount of current will flow damaging two diodes permanently. Diodes will eventually get open and no output will be available. | On Power failure CLB will retain its state. If particular MVAR is in injection and then power failure of its CLB occurs then it will not effect operation and system will remain in injection. If particular MVAR is bypassed its CLB is closed and system is injecting with reduced MVAR and then power failure occurs on closed CLB then system will retain its state and keeps injecting with reduced MVAR. | System will keep working normally. If CLB is stuck in closed state then system will keep injecting with reduced MVAR. . | 2 | Large reverse voltage. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | Failure will be detected by firmware by verifying the CARD_HEALTHY feedback (High when power fails). | 2 | 4 | CLB03? | CLB Card Unhealthy | [9 empty] | 5598
SV104-11107 |  |  |  | Diode fails-short and then fault occurs that engages CLB. | Auxiliary winding will get shorted if any diode fails-short. As a result of shortage, excessive amount of current will flow damaging two diodes permanently. Diodes will eventually get open and no output will be available. | If CLB is open, power failure occur and system is in injection and due to iiSC fault now faulty MVAR cannot be bypassed so system will transit to monitoring mode. System cannot go to injection anymore until the fault is cleared. | System will lose injection capability until the MVAR fault is cleared. | 4 | Large reverse voltage. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 4 | HALT. Electrical Stress Testing. Thermal Stress Testing. | Failure will be detected by firmware by verifying the CARD_HEALTHY feedback (High when power fails). | 2 | 8 | CLB03? | CLB Card Unhealthy | [7 empty] | 0 |  | 11107
SV104 - 5599 | Output Side Capacitor. | C17,C18 | To suppress output side ripples and to provide filtration. | Capacitor fails-open. | Output voltage may have ripples. No immediate effect on HV transformer board output. | If no other failure is observed on the board, CLB driver board will stay powered. Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | Mechanical stress. Localized heating for long time will separate end connection of capacitor. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [9 empty] | 0 |  | 5599
SV104 - 5600 |  |  |  | Capacitor fails-short | No voltage available at the output for the shorted duration. | On Power failure CLB will retain its state. If particular MVAR is in injection and then power failure of its CLB occurs then it will not effect operation and system will remain in injection. If particular MVAR is bypassed its CLB is closed and system is injecting with reduced MVAR and then power failure occurs on closed CLB then system will retain its state and keeps injecting with reduced MVAR. | System will keep working normally. If CLB is stuck in closed state then system will keep injecting with reduced MVAR. . | 2 | Wear-out due to dielectric degradation. High-voltage transients. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | Failure will be detected by firmware by verifying the CARD_HEALTHY feedback (High when power fails). | 2 | 4 | CLB03? | CLB Card Unhealthy | [9 empty] | 5600
SV104-11108 |  |  |  | Capacitor fails-short and then fault occurs that engages CLB. | No voltage available at the output for the shorted duration. | If CLB is open, power failure occur and system is in injection and due to iiSC fault now faulty MVAR cannot be bypassed so system will transit to monitoring mode. System cannot go to injection anymore until the fault is cleared. | System will lose injection capability until the MVAR fault is cleared. | 4 | Wear-out due to dielectric degradation. High-voltage transients. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 4 | HALT. Electrical Stress Testing. Thermal Stress Testing. | Failure will be detected by firmware by verifying the CARD_HEALTHY feedback (High when power fails). | 2 | 8 | CLB03? | CLB Card Unhealthy | [7 empty] | 0 |  | 11108
SV104-11109 | Current Limiting resistance for LED (D9) | R44 | To limit current through the LED (D9) | Resistor fails-open | LED indication functionality will be compromised No immediate effect on HV transformer board output. | If no other failure is observed on the board, CLB driver board will stay powered. Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | Over voltage. Over Temperature. Over stress due to shock or vibration. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. Vibration testing. | None. | 5 | 5 | [11 empty] | 11109
SV104-11110 |  |  |  | Resistor fails-short | LED indication functionality will be compromised No immediate effect on HV transformer board output. | If no other failure is observed on the board, CLB driver board will stay powered. Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | Wear-out due to extensive use. Excessive humidity. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. Vibration testing. | None. | 5 | 5 | [9 empty] | 0 |  | 11110
SV104-11111 | LED for status indication of voltage produced | D9 | Visual indication for board output status | Diode fails-open | LED indication functionality will be compromised No immediate effect on HV transformer board output. | If no other failure is observed on the board, CLB driver board will stay powered. Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | Over voltage. Over Temperature. Over stress due to shock or vibration. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. Vibration testing. | None. | 5 | 5 | [11 empty] | 11111
SV104-11112 |  |  |  | Diode fails-short | LED indication functionality will be compromised No immediate effect on HV transformer board output. | If no other failure is observed on the board, CLB driver board will stay powered. Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | Wear-out due to extensive use. Excessive humidity. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. Vibration testing. | None. | 5 | 5 | [9 empty] | 0 |  | 11112
SV104-11113 | Load at output | R42,R43 | To keep open load voltage within a range | Resistor fails-open | No immediate effect on board. | If no other failure is observed on the board, CLB driver board will stay powered. Device can operate in both monitoring and injection mode. | System will keep working normally. If CLB is stuck in closed state then system will keep injecting with reduced MVAR. . | 2 | Over voltage. Over Temperature. Over stress due to shock or vibration. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. Vibration testing. | None. | 5 | 10 | [11 empty] | 11113
SV104-11114 |  |  |  | resistor fails-open and then fault occurs that engages CLB. | No immediate effect on board. | If no other failure is observed on the board, CLB driver board will stay powered. Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | Over voltage. Over Temperature. Over stress due to shock or vibration. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. Vibration testing. | None. | 5 | 5 | [9 empty] | 0 |  | 11114
SV104-11115 |  |  |  | Resistor fails-short | 24V supply will be shorted out to ground. Resistance will eventually fail open due to over current. No output available at HV transformer board | On Power failure CLB will retain its state. If particular MVAR is in injection and then power failure of its CLB occurs then it will not effect operation and system will remain in injection. If particular MVAR is bypassed its CLB is closed and system is injecting with reduced MVAR and then power failure occurs on closed CLB then system will retain its state and keeps injecting with reduced MVAR. | System will keep working normally. If CLB is stuck in closed state then system will keep injecting with reduced MVAR. . | 2 | Wear-out due to extensive use. Excessive humidity. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. Vibration testing. | Failure will be detected by firmware by verifying the CARD_HEALTHY feedback (High when power fails). | 2 | 4 | CLB03? | CLB Card Unhealthy | [9 empty] | 11115
SV104-11116 |  |  |  | resistor fails-short and then fault occurs that engages CLB. | 24V supply will be shorted out to ground. Resistance will eventually fail open due to over current. No output available at HV transformer board | If CLB is open, power failure occur and system is in injection and due to iiSC fault now faulty MVAR cannot be bypassed so system will transit to monitoring mode. System cannot go to injection anymore until the fault is cleared. | System will lose injection capability until the MVAR fault is cleared. | 4 | Wear-out due to extensive use. Excessive humidity. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 4 | HALT. Electrical Stress Testing. Thermal Stress Testing. Vibration testing. | Failure will be detected by firmware by verifying the CARD_HEALTHY feedback (High when power fails). | 2 | 8 | CLB03? | CLB Card Unhealthy | [7 empty] | 0 |  | 11116
SV104 - 5601 | Heat Sink | HS1,HS2,HS3,HS4,HS5,HS6,HS7,HS8. | To provide cooling functionality for power components. | Loose connection between heat sink and power component | Affected component will face high temperature rise during nominal current operations. Power component may get damaged causing HV transformer board output voltage to drop. | On Power failure CLB will retain its state. If particular MVAR is in injection and then power failure of its CLB occurs then it will not effect operation and system will remain in injection. If particular MVAR is bypassed its CLB is closed and system is injecting with reduced MVAR and then power failure occurs on closed CLB then system will retain its state and keeps injecting with reduced MVAR. | System will keep working normally. If CLB is stuck in closed state then system will keep injecting with reduced MVAR. . | 2 | External overstress. Mis-handling. Excessive temperature causing joint melts. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | Failure will be detected by firmware by verifying the CARD_HEALTHY feedback (High when power fails). | 2 | 4 | CLB03? | CLB Card Unhealthy | [9 empty] | 5601
SV104-11117 |  |  |  | Loose connection between heat sink and power component and then fault occurs that engages CLB. | Affected component will face high temperature rise during nominal current operations. Power component may get damaged causing HV transformer board output voltage to drop. | If CLB is open, power failure occur and system is in injection and due to iiSC fault now faulty MVAR cannot be bypassed so system will transit to monitoring mode. System cannot go to injection anymore until the fault is cleared. | System will lose injection capability until the MVAR fault is cleared. | 4 | External overstress. Mis-handling. Excessive temperature causing joint melts. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 4 | HALT. Electrical Stress Testing. Thermal Stress Testing. | Failure will be detected by firmware by verifying the CARD_HEALTHY feedback (High when power fails). | 2 | 8 | CLB03? | CLB Card Unhealthy | [7 empty] | 0 |  | 11117
SV104-11435 | Secondary Winding Connector | J2 | Secondary of transformer | Connector Disconnected by external Force. | Secondary winding will be opened. No output available at HV transformer board. | On Power failure CLB will retain its state. If particular MVAR is in injection and then power failure of its CLB occurs then it will not effect operation and system will remain in injection. If particular MVAR is bypassed its CLB is closed and system is injecting with reduced MVAR and then power failure occurs on closed CLB then system will retain its state and keeps injecting with reduced MVAR. | System will keep working normally. If CLB is stuck in closed state then system will keep injecting with reduced MVAR. . | 2 | Open Connections due to vibrations, mis-handling or mechanical stress. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. Vibration Testing. | Failure will be detected by firmware by verifying the CARD_HEALTHY feedback (High when power fails). | 2 | 4 | CLB03? | CLB Card Unhealthy | [9 empty] | 11435
SV104-11436 |  |  |  | Connector disconnected by external force and then fault occurs that engages CLB. | Secondary winding will be opened. No output available at HV transformer board. | If CLB is open, power failure occur and system is in injection and due to iiSC fault now faulty MVAR cannot be bypassed so system will transit to monitoring mode. System cannot go to injection anymore until the fault is cleared. | System will lose injection capability until the MVAR fault is cleared. | 4 | Open Connections due to vibrations, mis-handling or mechanical stress. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 4 | HALT. Electrical Stress Testing. Thermal Stress Testing. | Failure will be detected by firmware by verifying the CARD_HEALTHY feedback (High when power fails). | 2 | 8 | CLB03? | CLB Card Unhealthy | [7 empty] | 0 |  | 11436
SV104-11437 |  |  |  | Connector Burned out | Due to sparking connector will heat up and eventually burnout No output available at HV transformer board. | On Power failure CLB will retain its state. If particular MVAR is in injection and then power failure of its CLB occurs then it will not effect operation and system will remain in injection. If particular MVAR is bypassed its CLB is closed and system is injecting with reduced MVAR and then power failure occurs on closed CLB then system will retain its state and keeps injecting with reduced MVAR. | System will keep working normally. If CLB is stuck in closed state then system will keep injecting with reduced MVAR. . | 2 | Connection Loose or Sparking at terminals Open Connections due to vibrations, mis-handling or mechanical stress. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. Vibration Testing. | Failure will be detected by firmware by verifying the CARD_HEALTHY feedback (High when power fails). | 2 | 4 | CLB03? | CLB Card Unhealthy | [9 empty] | 11437
SV104-11438 |  |  |  | Connector burned out and then fault occurs that engages CLB. | Due to sparking connector will heat up and eventually burnout No output available at HV transformer board. | If CLB is open, power failure occur and system is in injection and due to iiSC fault now faulty MVAR cannot be bypassed so system will transit to monitoring mode. System cannot go to injection anymore until the fault is cleared. | System will lose injection capability until the MVAR fault is cleared. | 4 | Connection Loose or Sparking at terminals Open Connections due to vibrations, mis-handling or mechanical stress. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 4 | HALT. Electrical Stress Testing. Thermal Stress Testing. | Failure will be detected by firmware by verifying the CARD_HEALTHY feedback (High when power fails). | 2 | 8 | CLB03? | CLB Card Unhealthy | [7 empty] | 0 |  | 11438
SV104-11439 | Low voltage DC output Connector | J4 | Output of HVT board | Connector Disconnected by external Force. | Output path will be broken. No output available at HV transformer board. | On Power failure CLB will retain its state. If particular MVAR is in injection and then power failure of its CLB occurs then it will not effect operation and system will remain in injection. If particular MVAR is bypassed its CLB is closed and system is injecting with reduced MVAR and then power failure occurs on closed CLB then system will retain its state and keeps injecting with reduced MVAR. | System will keep working normally. If CLB is stuck in closed state then system will keep injecting with reduced MVAR. . | 2 | Open Connections due to vibrations, mis-handling or mechanical stress. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. Vibration Testing. | Failure will be detected by firmware by verifying the CARD_HEALTHY feedback (High when power fails). | 2 | 4 | CLB03? | CLB Card Unhealthy | [9 empty] | 11439
SV104-11440 |  |  |  | Connector disconnected by external force and then fault occurs that engages CLB. | Output path will be broken. No output available at HV transformer board. | If CLB is open, power failure occur and system is in injection and due to iiSC fault now faulty MVAR cannot be bypassed so system will transit to monitoring mode. System cannot go to injection anymore until the fault is cleared. | System will lose injection capability until the MVAR fault is cleared. | 4 | Open Connections due to vibrations, mis-handling or mechanical stress. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 4 | HALT. Electrical Stress Testing. Thermal Stress Testing. | Failure will be detected by firmware by verifying the CARD_HEALTHY feedback (High when power fails). | 2 | 8 | CLB03? | CLB Card Unhealthy | [7 empty] | 0 |  | 11440
SV104-11441 |  |  |  | Connector Burned out | Due to sparking connector will heat up and eventually burnout Output path will be broken. No output available at HV transformer board. | On Power failure CLB will retain its state. If particular MVAR is in injection and then power failure of its CLB occurs then it will not effect operation and system will remain in injection. If particular MVAR is bypassed its CLB is closed and system is injecting with reduced MVAR and then power failure occurs on closed CLB then system will retain its state and keeps injecting with reduced MVAR. | System will keep working normally. If CLB is stuck in closed state then system will keep injecting with reduced MVAR. . | 2 | Connection Loose or Sparking at terminals Open Connections due to vibrations, mis-handling or mechanical stress. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. Vibration Testing. | Failure will be detected by firmware by verifying the CARD_HEALTHY feedback (High when power fails). | 2 | 4 | CLB03? | CLB Card Unhealthy | [9 empty] | 11441
SV104-11442 |  |  |  | Connector burned out and then fault occurs that engages CLB. | Due to sparking connector will heat up and eventually burnout Output path will be broken. No output available at HV transformer board. | If CLB is open, power failure occur and system is in injection and due to iiSC fault now faulty MVAR cannot be bypassed so system will transit to monitoring mode. System cannot go to injection anymore until the fault is cleared. | System will lose injection capability until the MVAR fault is cleared. | 4 | Connection Loose or Sparking at terminals Open Connections due to vibrations, mis-handling or mechanical stress. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 4 | HALT. Electrical Stress Testing. Thermal Stress Testing. | Failure will be detected by firmware by verifying the CARD_HEALTHY feedback (High when power fails). | 2 | 8 | CLB03? | CLB Card Unhealthy | [7 empty] | 0 |  | 11442
SV104-11443 | Auxiliary winding Connector | J6 | Auxiliary winding of transformer for 24AUX | Connector Disconnected by external Force. | 24AUX path will be broken. Startup circuitry will turn on permanently resulting in overheating and permanently damage to startup resistor. No output available once HV-ISO reboot. | On Power failure CLB will retain its state. If particular MVAR is in injection and then power failure of its CLB occurs then it will not effect operation and system will remain in injection. If particular MVAR is bypassed its CLB is closed and system is injecting with reduced MVAR and then power failure occurs on closed CLB then system will retain its state and keeps injecting with reduced MVAR. | System will keep working normally. If CLB is stuck in closed state then system will keep injecting with reduced MVAR. . | 2 | Open Connections due to vibrations, mis-handling or mechanical stress. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. Vibration Testing. | Failure will be detected by firmware by verifying the CARD_HEALTHY feedback (High when power fails). | 2 | 4 | CLB03? | CLB Card Unhealthy | [9 empty] | 11443
SV104-11444 |  |  |  | Connector disconnected by external force and then fault occurs that engages CLB. | 24AUX path will be broken. Startup circuitry will turn on permanently resulting in overheating and permanently damage to startup resistor. No output available once HV-ISO reboot. | If CLB is open, power failure occur and system is in injection and due to iiSC fault now faulty MVAR cannot be bypassed so system will transit to monitoring mode. System cannot go to injection anymore until the fault is cleared. | System will lose injection capability until the MVAR fault is cleared. | 4 | Open Connections due to vibrations, mis-handling or mechanical stress. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 4 | HALT. Electrical Stress Testing. Thermal Stress Testing. | Failure will be detected by firmware by verifying the CARD_HEALTHY feedback (High when power fails). | 2 | 8 | CLB03? | CLB Card Unhealthy | [9 empty] | 11444
SV104-11445 |  |  |  | Connector Burned out | Due to sparking connector will heat up and eventually burnout 24AUX path will be broken. Startup circuitry will turn on permanently resulting in overheating and permanently damage to startup resistor. No output available once HV-ISO reboot. | On Power failure CLB will retain its state. If particular MVAR is in injection and then power failure of its CLB occurs then it will not effect operation and system will remain in injection. If particular MVAR is bypassed its CLB is closed and system is injecting with reduced MVAR and then power failure occurs on closed CLB then system will retain its state and keeps injecting with reduced MVAR. | System will keep working normally. If CLB is stuck in closed state then system will keep injecting with reduced MVAR. . | 2 | Connection Loose or Sparking at terminals Open Connections due to vibrations, mis-handling or mechanical stress. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. Vibration Testing. | Failure will be detected by firmware by verifying the CARD_HEALTHY feedback (High when power fails). | 2 | 4 | CLB03? | CLB Card Unhealthy | [9 empty] | 11445
SV104-11446 |  |  |  | Connector burned out and then fault occurs that engages CLB. | Due to sparking connector will heat up and eventually burnout 24AUX path will be broken. Startup circuitry will turn on permanently resulting in overheating and permanently damage to startup resistor. No output available once HV-ISO reboot. | If CLB is open, power failure occur and system is in injection and due to iiSC fault now faulty MVAR cannot be bypassed so system will transit to monitoring mode. System cannot go to injection anymore until the fault is cleared. | System will lose injection capability until the MVAR fault is cleared. | 4 | Connection Loose or Sparking at terminals Open Connections due to vibrations, mis-handling or mechanical stress. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 4 | HALT. Electrical Stress Testing. Thermal Stress Testing. | Failure will be detected by firmware by verifying the CARD_HEALTHY feedback (High when power fails). | 2 | 8 | CLB03? | CLB Card Unhealthy | [7 empty] | 0 |  | 11446
SV104-11447 | Primary winding of transformer | J1,J5 | primary winding of transformer | Connector Disconnected by external Force. | No voltage will be available at transformer output. No output available at HV transformer board. | On Power failure CLB will retain its state. If particular MVAR is in injection and then power failure of its CLB occurs then it will not effect operation and system will remain in injection. If particular MVAR is bypassed its CLB is closed and system is injecting with reduced MVAR and then power failure occurs on closed CLB then system will retain its state and keeps injecting with reduced MVAR. | System will keep working normally. If CLB is stuck in closed state then system will keep injecting with reduced MVAR. . | 2 | Open Connections due to vibrations, mis-handling or mechanical stress. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. Vibration Testing. | Failure will be detected by firmware by verifying the CARD_HEALTHY feedback (High when power fails). | 2 | 4 | CLB03? | CLB Card Unhealthy | [9 empty] | 11447
SV104-11448 |  |  |  | Connector disconnected by external force and then fault occurs that engages CLB. | No voltage will be available at transformer output. No output available at HV transformer board. | If CLB is open, power failure occur and system is in injection and due to iiSC fault now faulty MVAR cannot be bypassed so system will transit to monitoring mode. System cannot go to injection anymore until the fault is cleared. | System will lose injection capability until the MVAR fault is cleared. | 4 | Open Connections due to vibrations, mis-handling or mechanical stress. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 4 | HALT. Electrical Stress Testing. Thermal Stress Testing. | Failure will be detected by firmware by verifying the CARD_HEALTHY feedback (High when power fails). | 2 | 8 | CLB03? | CLB Card Unhealthy | [9 empty] | 11448
SV104-11449 |  |  |  | Connector Burned out | Due to sparking connector will heat up and eventually burnout No voltage will be available at transformer output. No output available at HV transformer board. | On Power failure CLB will retain its state. If particular MVAR is in injection and then power failure of its CLB occurs then it will not effect operation and system will remain in injection. If particular MVAR is bypassed its CLB is closed and system is injecting with reduced MVAR and then power failure occurs on closed CLB then system will retain its state and keeps injecting with reduced MVAR. | System will keep working normally. If CLB is stuck in closed state then system will keep injecting with reduced MVAR. . | 2 | Connection Loose or Sparking at terminals Open Connections due to vibrations, mis-handling or mechanical stress. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. Vibration Testing. | Failure will be detected by firmware by verifying the CARD_HEALTHY feedback (High when power fails). | 2 | 4 | CLB03? | CLB Card Unhealthy | [9 empty] | 11449
SV104-11450 |  |  |  | Connector burned out and then fault occurs that engages CLB. | Due to sparking connector will heat up and eventually burnout No voltage will be available at transformer output. No output available at HV transformer board. | If CLB is open, power failure occur and system is in injection and due to iiSC fault now faulty MVAR cannot be bypassed so system will transit to monitoring mode. System cannot go to injection anymore until the fault is cleared. | System will lose injection capability until the MVAR fault is cleared. | 4 | Connection Loose or Sparking at terminals Open Connections due to vibrations, mis-handling or mechanical stress. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 4 | HALT. Electrical Stress Testing. Thermal Stress Testing. | Failure will be detected by firmware by verifying the CARD_HEALTHY feedback (High when power fails). | 2 | 8 | CLB03? | CLB Card Unhealthy | [9 empty] | 11450
SV104 - 6989 | Connector | J3 | Input connector | Disconnected by external force | No output available at HV transformer board. | On Power failure CLB will retain its state. If particular MVAR is in injection and then power failure of its CLB occurs then it will not effect operation and system will remain in injection. If particular MVAR is bypassed its CLB is closed and system is injecting with reduced MVAR and then power failure occurs on closed CLB then system will retain its state and keeps injecting with reduced MVAR. | System will keep working normally. If CLB is stuck in closed state then system will keep injecting with reduced MVAR. . | 2 | External overstress. Mis-handling. Excessive temperature causing joint melts. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | Failure will be detected by firmware by verifying the CARD_HEALTHY feedback (High when power fails). | 2 | 4 | CLB03? | CLB Card Unhealthy | [9 empty] | 6989
SV104-11118 |  |  |  | Connector disconnected by external force and then fault occurs that engages CLB. | No output available at HV transformer board. | If CLB is open, power failure occur and system is in injection and due to iiSC fault now faulty MVAR cannot be bypassed so system will transit to monitoring mode. System cannot go to injection anymore until the fault is cleared. | System will lose injection capability until the MVAR fault is cleared. | 4 | External overstress. Mis-handling. Excessive temperature causing joint melts. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 4 | HALT. Electrical Stress Testing. Thermal Stress Testing. | Failure will be detected by firmware by verifying the CARD_HEALTHY feedback (High when power fails). | 2 | 8 | CLB03? | CLB Card Unhealthy | [9 empty] | 11118
SV104 - 6990 |  |  |  | Connector shorted | PHT-DC board external capacitor will dump full energy in board. HV-ISO board's input traces will burn out. Board will be damaged permanently. | On Power failure CLB will retain its state. If particular MVAR is in injection and then power failure of its CLB occurs then it will not effect operation and system will remain in injection. If particular MVAR is bypassed its CLB is closed and system is injecting with reduced MVAR and then power failure occurs on closed CLB then system will retain its state and keeps injecting with reduced MVAR. | System will keep working normally. If CLB is stuck in closed state then system will keep injecting with reduced MVAR. . | 2 | Manufacturing Deficiency. Excessive temperature causing joint melts. Excessive humidity. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Conformal coating whole connector and mask only mating part of pins. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | Failure will be detected by firmware by verifying the CARD_HEALTHY feedback (High when power fails). | 2 | 4 | CLB03? | CLB Card Unhealthy | [9 empty] | 6990
SV104-11119 |  |  |  | Connector shorted and then fault occurs that engages CLB. | PHT-DC board external capacitor will dump full energy in board. HV-ISO board's input traces will burn out. Board will be damaged permanently. | If CLB is open, power failure occur and system is in injection and due to iiSC fault now faulty MVAR cannot be bypassed so system will transit to monitoring mode. System cannot go to injection anymore until the fault is cleared. | System will lose injection capability until the MVAR fault is cleared. | 4 | Electrical Overstress (Overvoltage). ESD. Counterfeit part. Stress or impact during assembly. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 4 | HALT. Electrical Stress Testing. Thermal Stress Testing. | Failure will be detected by firmware by verifying the CARD_HEALTHY feedback (High when power fails). | 2 | 8 | CLB03? | CLB Card Unhealthy | [9 empty] | 11119
| HV Transformer Board for iiDCE Board | [26 empty] | 0
| 15 V On-Board Supply | [26 empty] | 0
SV104 - 5602 | Input Side TRIACs. | D13,D12 | Reverse polarity protection. | TRIAC fails-open. | No immediate effect. Parallel TRIAC available for alternate path. | If no other failure is observed on the board, iiDCE board will stay powered. Device can operate in both monitoring and injection mode | System will keep working normally. | 1 | On-board fault causing higher current flow. Excessive forward current. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iiDCE driver board. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [11 empty] | 5602
SV104 - 5603 |  |  |  | TRIAC fails-short. | Reverse polarity protection will be compromised during shortage. Board will keep working normally if input is provided with correct polarity. | If no other failure is observed on the board, iiDCE board will stay powered. Device can operate in both monitoring and injection mode | System will keep working normally. | 1 | Large reverse voltage. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iiDCE driver board. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [9 empty] | 0 |  | 5603
SV104 - 6991 |  |  |  | Both TRIACs fail-short. | Reverse polarity protection will be compromised. Board will keep working normally if input is provided with correct polarity. | If no other failure is observed on the board, iiDCE board will stay powered. Device can operate in both monitoring and injection mode | System will keep working normally. | 1 | Large reverse voltage. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iiDCE driver board. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [11 empty] | 6991
SV104 - 6992 |  |  |  | Both TRIACs fail-open | Input path will be broken. No output available at HV transformer board. | iiDCE will be unable to get power from redundant HVT board, but will get power from other HVT board (in sharing with clamp board). Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | On-board fault causing higher current flow. Excessive forward current. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iiDCE driver board. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [9 empty] | 0 |  | 6992
SV104 - 5604 | Input Side Fuse. | F2 | To cut-off supply in case of over-current. | Fuse fails-open. | Input power path will be broken. No output available at HV transformer board. | iiDCE will be unable to get power from redundant HVT board, but will get power from other HVT board (in sharing with clamp board). Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | On-board fault causing higher current flow. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iiDCE driver board. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 10 | [11 empty] | 5604
SV104 - 5605 | Input Side Filter Capacitors. | C2,C23 | To suppress ripples on input voltage. To store energy for power demand. | Capacitor fails-open. | Input supply ripples may cause distorted output supply. No immediate effect on board.. | If no other failure is observed on the board, iiDCE board will stay powered. Device can operate in both monitoring and injection mode | System will keep working normally. | 1 | Mechanical stress. Localized heating for long time will separate end connection of capacitor. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iiDCE driver board. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [9 empty] | 0 |  | 5605
SV104 - 5606 |  |  |  | Capacitor fails-short. | PHT-DC Capacitor will dump full energy in HV-ISO board leaving it permanently damage (Trace damage). No output available at HV transformer board. | If no other failure is observed on the board, iiDCE board will stay powered. Device can operate in both monitoring and injection mode | System will keep working normally. | 1 | Wear-out due to dielectric degradation. High-voltage transients. De-gradation of components. Water ingress during humidity condition as it is film capacitor. Overvoltage | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. RTV application on edges to stop water ingress. Redundant HV Transformer board to power-up iiDCE driver board. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. Environmental Testing. | None. | 5 | 5 | [11 empty] | 5606
SV104 - 5607 | Low Voltage Detection Zener Diode. (D7, D11, D10) | D7,D10,D11 | To set under-voltage lockout threshold. | Diode fails-open. | No voltage will be available at power controlling MOSFET gate. On-board 15 V supply will not be available. No output available at HV transformer board. | iiDCE will be unable to get power from redundant HVT board, but will get power from other HVT board (in sharing with clamp board). Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | On-board fault causing higher current flow. Excessive forward current. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iiDCE driver board. | 2 | 4 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 20 | [9 empty] | 0 |  | 5607
SV104 - 5608 |  |  |  | Diode fails-short.. | The threshold for UVLO detection will decrease. Board will turn on before the set threshold of 320 V. Slight effect will be on PHT-DC bus during low line current condition as it will ramp up slowly. Board will keep working. | If no other failure is observed on the board, iiDCE board will stay powered. Device can operate in both monitoring and injection mode | System will keep working normally. | 2 | Large reverse voltage. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iiDCE driver board. | 2 | 4 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 20 | [11 empty] | 5608
SV104-11120 | Low Voltage Detection Voltage Divider | R41,R36 | To set UVLO threshold | Resistor fails-open. | No voltage will be available at power controlling MOSFET gate. On-board 15 V supply will not be available. No output available at HV transformer board. | iiDCE will be unable to get power from redundant HVT board, but will get power from other HVT board (in sharing with clamp board). Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Over voltage. Over Temperature. Over stress due to shock or vibration. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iiDCE driver board. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. Vibration testing. | None. | 5 | 10 | [9 empty] | 0 |  | 11120
SV104-11121 |  |  |  | Resistor fails-short. | UVLO limit will decrease. Board will powerup at lower voltage. Board will keep working. | If no other failure is observed on the board, iiDCE board will stay powered. Device can operate in both monitoring and injection mode | System will keep working normally. | 1 | Wear-out due to extensive use. Excessive humidity. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iiDCE driver board. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. Vibration testing. | None. | 5 | 5 | [11 empty] | 11121
SV104 - 5609 | Input Side Voltage Divider Resistor. | R30,R31,R32,R33,R34,R35 | To step down voltage. | Resistor fails-open. | No voltage will be available at power controlling MOSFET gate. On-board 15 V supply will not be available. No output available at HV transformer board. | iiDCE will be unable to get power from redundant HVT board, but will get power from other HVT board (in sharing with clamp board). Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Over voltage. Over Temperature. Over stress due to shock or vibration. De-gradation of components. Overcurrent. Counterfeit part. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iiDCE driver board. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. Vibration testing. | None. | 5 | 10 | [9 empty] | 0 |  | 5609
SV104 - 5610 |  |  |  | Any one resistor fails-short. | No immediate effect on board. Board will keep working normally. | If no other failure is observed on the board, iiDCE board will stay powered. Device can operate in both monitoring and injection mode | System will keep working normally. | 1 | Wear-out due to extensive use. Excessive humidity. Counterfeit part. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Conformal coating. Redundant HV Transformer board to power-up iiDCE driver board. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. Vibration testing. | None. | 5 | 5 | [11 empty] | 5610
SV104-12407 |  |  |  | More than one resistors fails-short. | Soft starting current is increased significantly consequently MOSFET power dissipation will increase that could bring failure. No output available at HV transformer board. | iiDCE will be unable to get power from redundant HVT board, but will get power from other HVT board (in sharing with clamp board). Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Wear-out due to extensive use. Excessive humidity. Counterfeit part. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements.. Conformal coating. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. Vibration testing. | None. | 5 | 10 | [11 empty] | 12407
SV104 - 5611 | Input Power Control MOSFET. | Q6 | To turn ON/OFF power flow. | MOSFET fails-open. | Input power path will be broken. No output available at HV transformer board. | iiDCE will be unable to get power from redundant HVT board, but will get power from other HVT board (in sharing with clamp board). Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Overheating Mechanical stress resulting in cracked MOSFET body. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iiDCE driver board. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 10 | [11 empty] | 5611
SV104 - 5612 |  |  |  | MOSFET fails-short. | Startup circuitry will turn on permanently resulting in overheating and permanently damage to startup resistor. No output available once HV-ISO reboot. | iiDCE will be unable to get power from redundant HVT board, but will get power from other HVT board (in sharing with clamp board). Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Transients Overheating as a result of loose connection with heat sink Overcurrent Counterfeit part Damage during mechanical assembly of board Metallic debris stuck in between terminals | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iiDCE driver board. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 10 | [11 empty] | 5612
SV104 - 5613 | Over-voltage Protection Zener Diode at MOSFET Gate Side. | D31 | For gate protection of MOSFET. | Diode fails-open. | Over-voltage protection of MOSFET won't be available. No immediate effect on board in normal operations. | If no other failure is observed on the board, iiDCE board will stay powered. Device can operate in both monitoring and injection mode | System will keep working normally. | 1 | On-board fault causing higher current flow. Excessive forward current. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iiDCE driver board. | 2 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 10 | [11 empty] | 5613
SV104 - 5614 |  |  |  | Diode fails-short. | MOSFET will be turned off completely. Startup circuit will not work. No output available at HV transformer board. | iiDCE will be unable to get power from redundant HVT board, but will get power from other HVT board (in sharing with clamp board). Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Large reverse voltage. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iiDCE driver board. | 2 | 4 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 20 | [11 empty] | 5614
SV104-12408 | Filtration Capacitor | C21 | To suppress noise and remove ripples | Capacitor fails-open. | No immediate effect on board. Board will keep working normally. | If no other failure is observed on the board, iiDCE board will stay powered. Device can operate in both monitoring and injection mode | System will keep working normally. | 1 | Mechanical stress. Localized heating for long time will separate end connection of capacitor. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iiDCE driver board. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. Vibration Testing. | None. | 5 | 5 | [11 empty] | 12408
SV104-12409 |  |  |  | Capacitor fails-short. | HVDC and 24VAUX will be shorted top ground. Startup circuit will not work. Input Fuse Will be Blown No output available at HV transformer board. | iiDCE will be unable to get power from redundant HVT board, but will get power from other HVT board (in sharing with clamp board). Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Wear-out due to dielectric degradation. High-voltage transients. De-gradation of components. Water ingress during humidity condition as it is film capacitor. Overvoltage | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iiDCE driver board. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. Environmental Testing. | None. | 5 | 10 | [11 empty] | 12409
SV104-11122 | MOSFET resistance for Miller Capacitance | R37 | To discharge miller capacitance of MOSFET | Resistor fails-open | Abnormal Behavior of MOSFET Might turn ON/OFF abnormally. Once Board Reboots no output will be available No output available at HV transformer board | iiDCE will be unable to get power from redundant HVT board, but will get power from other HVT board (in sharing with clamp board). Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Over voltage. Over Temperature. Over stress due to shock or vibration. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iiDCE driver board. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. Vibration testing. | None. | 5 | 10 | [11 empty] | 11122
SV104-11123 |  |  |  | Resistor fails-short | Gate and Source of Q6 will have no voltage difference so MOSFET cannot operate No output available at HV transformer board | iiDCE will be unable to get power from redundant HVT board, but will get power from other HVT board (in sharing with clamp board). Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Wear-out due to extensive use. Excessive humidity. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iiDCE driver board. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. Vibration testing. | None. | 5 | 10 | [11 empty] | 11123
SV104 - 6993 | D21-Free wheeling diode | D21 | To protect BJT during reverse voltage condition | Diode fails-open. | No protection for BJT will be available. Reverse voltage development across BJT will damage it. No output available. | iiDCE will be unable to get power from redundant HVT board, but will get power from other HVT board (in sharing with clamp board). Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | On-board fault causing higher current flow. Excessive forward current. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iiDCE driver board. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 10 | [11 empty] | 6993
SV104 - 6994 |  |  |  | Diode fails-short. | Input will appear as it is on output which will damage PWM controller and gate driver ICs permanently. No output available. | iiDCE will be unable to get power from redundant HVT board, but will get power from other HVT board (in sharing with clamp board). Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Large reverse voltage. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iiDCE driver board. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 10 | [11 empty] | 6994
SV104 - 6995 | D22-To prevent reverse power flow | D22 | To prevent reverse power flow from auxiliary to startup circuitry | Diode fails-open. | Input power path will be broken. No output available at HV transformer board. | iiDCE will be unable to get power from redundant HVT board, but will get power from other HVT board (in sharing with clamp board). Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | On-board fault causing higher current flow. Excessive forward current. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iiDCE driver board. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 10 | [9 empty] | 0 |  | 6995
SV104 - 6996 |  |  |  | Diode fails-short. | If the board is OFF than it can not turn ON. If board is ON than reverse power will start to flow. D31 will be forward biased and as gate of Q6 is grounded than 24VAUX will also be grounded. No output available at HV transformer board. | iiDCE will be unable to get power from redundant HVT board, but will get power from other HVT board (in sharing with clamp board). Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Large reverse voltage. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iiDCE driver board. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 10 | [11 empty] | 6996
SV104 - 6997 | D27-Zener diode | D27 | To set reference voltage for BJT to regulate | Diode fails-open. | Voltage at input will appear as it is on base damaging it permanently. No output available at HV transformer board. | iiDCE will be unable to get power from redundant HVT board, but will get power from other HVT board (in sharing with clamp board). Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Electrical, Mechanical or environmental overstress. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iiDCE driver board. | 2 | 4 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 20 | [11 empty] | 6997
SV104 - 6998 |  |  |  | Diode fails-short. | BJT will not turn on. No output available at HV transformer board. | iiDCE will be unable to get power from redundant HVT board, but will get power from other HVT board (in sharing with clamp board). Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Excessive Temperature. Overcurrent. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iiDCE driver board. | 2 | 4 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 20 | [11 empty] | 6998
SV104 - 5615 | Input Power Control BJT. | Q8 | To provide regulated voltage for startup. | BJT fails-open. | Input power path will be broken. No output available at HV transformer board. | iiDCE will be unable to get power from redundant HVT board, but will get power from other HVT board (in sharing with clamp board). Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Melted connections due to overheating. Manufacturing defect. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iiDCE driver board. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 10 | [11 empty] | 5615
SV104 - 5616 |  |  |  | BJT fails-short. | Higher voltage at startup will damage the PWM controller and gate drivers of board. Input power path will be broken. No output available at HV transformer board. | iiDCE will be unable to get power from redundant HVT board, but will get power from other HVT board (in sharing with clamp board). Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Over voltage. Leaky junctions. Wear-out due to high power dissipation. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iiDCE driver board. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 10 | [9 empty] | 0 |  | 5616
SV104 - 5617 | Biasing Resistor for BJT. | R40 | To set biasing threshold for power flow controlling BJT. | Resistor fails-open. | BJT will be permanently turned OFF. Input power path will be broken. No output available at HV transformer board. | iiDCE will be unable to get power from redundant HVT board, but will get power from other HVT board (in sharing with clamp board). Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Over voltage. Over Temperature. Over stress due to shock or vibration. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iiDCE driver board. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 10 | [9 empty] | 0 |  | 5617
SV104 - 5618 |  |  |  | Resistor fails-short. | 24 V will be replicated at the emitter for the shorted duration, on-board ICs may get burn due to this over-voltage. BJT will eventually fail-open due to over-current. Input power path will be broken. No output available at HV transformer board. | iiDCE will be unable to get power from redundant HVT board, but will get power from other HVT board (in sharing with clamp board). Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Wear-out due to extensive use. Excessive humidity. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iiDCE driver board. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 10 | [9 empty] | 0 |  | 5618
SV104 - 5619 | Freewheeling Diode. |  | To provide reverser current flow path. | Diode fails-open. | No path will be available for reverse current to flow. Potential difference creation across BJT can damage the BJT. Input power path will be broken. No output available at HV transformer board. | iiDCE will be unable to get power from redundant HVT board, but will get power from other HVT board (in sharing with clamp board). Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Excessive forward current flow. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iiDCE driver board. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 10 | [9 empty] | 0 |  | 5619
SV104 - 5620 |  |  |  | Diode fails-short. | An emitter to collector short on BJT will cause the BJT to over-heat and may fail-open. Input power path will be broken. No output available at HV transformer board. | iiDCE will be unable to get power from redundant HVT board, but will get power from other HVT board (in sharing with clamp board). Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Large reverse voltage. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iiDCE driver board. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 10 | [11 empty] | 5620
SV104 - 5621 | 15 V Rail Output Side Capacitors. | C22,C19,C20 | To stable output voltage and to suppress ripples. | Capacitor fails-open. | No immediate effect on board.. | If no other failure is observed on the board, iiDCE board will stay powered. Device can operate in both monitoring and injection mode | System will keep working normally. | 1 | Mechanical stress. Localized heating for long time will separate end connection of capacitor. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iiDCE driver board. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [9 empty] | 0 |  | 5621
SV104 - 5622 |  |  |  | Capacitor fails-short. | 15 V power supply will be shorted to ground. On-board electronics will not be powered up. No output available at HV transformer board. | iiDCE will be unable to get power from redundant HVT board, but will get power from other HVT board (in sharing with clamp board). Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Wear-out due to dielectric degradation. High-voltage transients. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iiDCE driver board. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 10 | [11 empty] | 5622
SV104 - 5623 | 24 V Feedback Signal Side Resistor. | R38 | To provide 24 V sensing feedback path. | Resistor fails-open. | 15 V regulator will keep on working from input side and will not turn off. Which will heat up the resistor on MOSFET Q6 drain and will burn out eventually. No output available at HV transformer board. | iiDCE will be unable to get power from redundant HVT board, but will get power from other HVT board (in sharing with clamp board). Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Over voltage. Over Temperature. Over stress due to shock or vibration. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iiDCE driver board. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 10 | [9 empty] | 0 |  | 5623
SV104 - 5624 |  |  |  | Resistor fails-short. | Over-current will cause the resistor to eventually fail-open. 15 V regulator will keep on working from input side and will not turn off. Which will heat up the resistor on MOSFET Q6 drain and will burn out eventually. No output available at HV transformer board. | iiDCE will be unable to get power from redundant HVT board, but will get power from other HVT board (in sharing with clamp board). Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Wear-out due to extensive use. Excessive humidity. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iiDCE driver board. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 10 | [11 empty] | 5624
SV104 - 5625 | 24 V Feedback Signal Side 9 V Zener Diode. | D23 | To maintain a constant 9 V drop. To turn off the startup circuitry once full bridge auxiliary supply exceeds 9.1 V. | Diode fails-open. | 15 V regulator will keep on working from input side and will not turn off. Which will heat up the resistor on MOSFET Q6 drain and will burn out eventually. No output available at HV transformer board. | iiDCE will be unable to get power from redundant HVT board, but will get power from other HVT board (in sharing with clamp board). Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Electrical, Mechanical or environmental overstress. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iiDCE driver board. | 2 | 4 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 20 | [9 empty] | 0 |  | 5625
SV104 - 5626 |  |  |  | Diode fails-short. | Startup circuitry will be turned off before full bridge secondary is activated completely. As a result startup circuitry will keep activating and then turn off due to aux voltage. This will eventually damage the startup circuitry of board. No output available at HV transformer board. | iiDCE will be unable to get power from redundant HVT board, but will get power from other HVT board (in sharing with clamp board). Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Excessive Temperature. Overcurrent. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iiDCE driver board. | 2 | 4 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 20 | [11 empty] | 5626
SV104 - 6999 | 24 V Feedback Signal Side - R39 | R39 | Voltage divider resistor-Low side | Resistor fails-open | 15 V regulator will keep on working from input side and will not turn off. Which will heat up the resistor on MOSFET Q6 drain and will burn out eventually. No output available at HV transformer board. | iiDCE will be unable to get power from redundant HVT board, but will get power from other HVT board (in sharing with clamp board). Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Over voltage. Over Temperature. Over stress due to shock or vibration. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iiDCE driver board. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 10 | [11 empty] | 6999
SV104 - 7000 |  |  |  | Resistor fails-short | 15 V regulator will keep on working from input side and will not turn off. Which will heat up the resistor on MOSFET Q6 drain and will burn out eventually. No output available at HV transformer board. | iiDCE will be unable to get power from redundant HVT board, but will get power from other HVT board (in sharing with clamp board). Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Wear-out due to extensive use. Excessive humidity. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iiDCE driver board. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 10 | [11 empty] | 7000
SV104 - 7001 | 24 V Feedback Signal Side - D23 | D23 | To maintain a constant 9 V drop. To turn off the startup circuitry once full bridge auxiliary supply exceeds 9.1 V. | Diode fails-open | 15 V regulator will keep on working from input side and will not turn off. Which will heat up the resistor on MOSFET Q6 drain and will burn out eventually. No output available at HV transformer board. | iiDCE will be unable to get power from redundant HVT board, but will get power from other HVT board (in sharing with clamp board). Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Excessive forward current flow. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iiDCE driver board. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 10 | [9 empty] | 0 |  | 7001
SV104 - 7002 |  |  |  | Diode fails-short | No immediate effect on board. | If no other failure is observed on the board, iiDCE board will stay powered. Device can operate in both monitoring and injection mode | System will keep working normally. | 1 | Large reverse voltage. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iiDCE driver board. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [11 empty] | 7002
SV104 - 7003 | 24 V Feedback Signal Side - D24 | D24 | To prevent reverse power flow from startup circuitry | Diode fails-open | As soon as auxiliary will develop board will be disabled and power-up again and this cycle will keep repeating which will damage the startup circuitry permanently. No output available at HV transformer board. | iiDCE will be unable to get power from redundant HVT board, but will get power from other HVT board (in sharing with clamp board). Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Excessive forward current flow. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iiDCE driver board. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 10 | [9 empty] | 0 |  | 7003
SV104 - 7004 |  |  |  | Diode fails-short | Startup circuitry will disable itself before powering up the board. It will happen repeatedly eventually damaging the startup circuitry. No output available at HV transformer board. | iiDCE will be unable to get power from redundant HVT board, but will get power from other HVT board (in sharing with clamp board). Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Large reverse voltage. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iiDCE driver board. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 10 | [11 empty] | 7004
SV104 - 7005 | 24 V Feedback Signal Side - D26 | D26 | Overvoltage protection for MOSFET | Diode fails-open | No immediate effect on board. | If no other failure is observed on the board, iiDCE board will stay powered. Device can operate in both monitoring and injection mode | System will keep working normally. | 1 | Excessive forward current flow. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iiDCE driver board. | 2 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 10 | [11 empty] | 7005
SV104 - 7006 |  |  |  | Diode fails-short | 15 V regulator will keep on working from input side and will not turn off. Which will heat up the resistor on MOSFET Q6 drain and will burn out eventually. No output available at HV transformer board. | iiDCE will be unable to get power from redundant HVT board, but will get power from other HVT board (in sharing with clamp board). Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Large reverse voltage. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iiDCE driver board. | 2 | 4 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 20 | [11 empty] | 7006
SV104 - 5627 | 24 V Feedback Signal Side MOSFET. | Q7 | To turn OFF power flow controlling MOSFET when auxiliary voltage develops. | MOSFET fails-open. | 15 V regulator will keep on working from input side and will not turn off. Which will heat up the resistor on MOSFET Q6 drain and will burn out eventually. No output available at HV transformer board. | iiDCE will be unable to get power from redundant HVT board, but will get power from other HVT board (in sharing with clamp board). Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Overheating Mechanical stress resulting in cracked MOSFET body. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iiDCE driver board. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 10 | [9 empty] | 0 |  | 5627
SV104 - 5628 |  |  |  | MOSFET fails-short. | Startup circuitry will remain off permanently as Q6 remains off permanently. 15 V regulator will keep on working from input side and will not turn off. Which will heat up the resistor on MOSFET Q6 drain and will burn out eventually. No output available at HV transformer board. | iiDCE will be unable to get power from redundant HVT board, but will get power from other HVT board (in sharing with clamp board). Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Transients Overheating as a result of loose connection with heat sink Overcurrent Counterfeit part Damage during mechanical assembly of board Metallic debris stuck in between terminals | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iiDCE driver board. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 10 | [11 empty] | 5628
SV104 - 5629 | 24 V Feedback Signal Side MOSFET.- Zener at Gate | D25 | To protect MOSFET (Q6) gate from over-voltage. | Diode fails-open. | Over-voltage protection of MOSFET won't be available. No immediate effect on board in normal operations. | If no other failure is observed on the board, iiDCE board will stay powered. Device can operate in both monitoring and injection mode | System will keep working normally. | 1 | Excessive forward current flow. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iiDCE driver board. | 2 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 10 | [9 empty] | 0 |  | 5629
SV104 - 5630 |  |  |  | Diode fails-short. | Board will not power up as startup circuit will remain off. Q6 will remain permanently off. No output available at HV transformer board. | iiDCE will be unable to get power from redundant HVT board, but will get power from other HVT board (in sharing with clamp board). Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Large reverse voltage. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iiDCE driver board. | 2 | 4 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 20 | [11 empty] | 5630
| PWM Controller | [26 empty] | 0
SV104 - 5631 | PWM Controller IC. | U1 | To provide alternate PWM pulses for full bridge gate driver. | IC output is permanently low. | No PWM will be available for half bridge driver ICs, No output available at HV transformer board. | iiDCE will be unable to get power from redundant HVT board, but will get power from other HVT board (in sharing with clamp board). Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Electrical Overstress. ESD. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iiDCE driver board. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 10 | [9 empty] | 0 |  | 5631
SV104 - 5632 |  |  |  | One of output is permanently high. | Output of Full Bridge circuit will be 12 V at no load. HV transformer board will have no output as soon as load is applied. | iiDCE will be unable to get power from redundant HVT board, but will get power from other HVT board (in sharing with clamp board). Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Electrical Overstress. ESD. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iiDCE driver board. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 10 | [11 empty] | 5632
SV104 - 5633 |  |  |  | PWM is having different duty cycle than desired. | Output of Full Bridge circuit will have different duty cycle. HV transformer board will have more or less than 24 V output. | If no other failure is observed on the board, iiDCE board will stay powered. Device can operate in both monitoring and injection mode | System will keep working normally. | 1 | Internal IC damage. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iiDCE driver board. | 2 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 10 | [11 empty] | 5633
SV104 - 5634 | Line Under-Voltage Lockout Voltage Divider High Side Resistor. | R1 | To turn OFF gate driver PWM in case of under-voltage. | Resistor fails-open. | PWM controller will remain off permanently. No output available. | iiDCE will be unable to get power from redundant HVT board, but will get power from other HVT board (in sharing with clamp board). Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Over voltage. Over Temperature. Over stress due to shock or vibration. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iiDCE driver board. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 10 | [11 empty] | 5634
SV104 - 5635 |  |  |  | Resistor fails-short. | UVLO pin will get damaged, No PWM will be available for half bridge driver ICs, No output available at HV transformer board. | iiDCE will be unable to get power from redundant HVT board, but will get power from other HVT board (in sharing with clamp board). Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Wear-out due to extensive use. Excessive humidity. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iiDCE driver board. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 10 | [11 empty] | 5635
SV104 - 5636 | Line Under-Voltage Lockout Voltage Divider Low Side Resistor. | R13 | To turn OFF gate driver PWM in case of under-voltage. | Resistor fails-open. | UVLO pin will get damaged, No PWM will be available for half bridge driver ICs, No output available at HV transformer board. | iiDCE will be unable to get power from redundant HVT board, but will get power from other HVT board (in sharing with clamp board). Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Over voltage. Over Temperature. Over stress due to shock or vibration. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iiDCE driver board. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 10 | [11 empty] | 5636
SV104 - 5637 |  |  |  | Resistor fails-short. | PWM controller will remain off permanently. No output available. | iiDCE will be unable to get power from redundant HVT board, but will get power from other HVT board (in sharing with clamp board). Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Wear-out due to extensive use. Excessive humidity. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iiDCE driver board. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 10 | [9 empty] | 0 |  | 5637
SV104 - 5638 | RT2 Biasing Resistor. | R14 | To control oscillator dead time. | Resistor fails-open. | Dead time between alternating PWMs will be altered (maximum). 1 PWM will be permanently high, while other will be permanently low. Output of isolation transformer will not be available. No output available at HV transformer board. | iiDCE will be unable to get power from redundant HVT board, but will get power from other HVT board (in sharing with clamp board). Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Over voltage. Over Temperature. Over stress due to shock or vibration. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iiDCE driver board. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 10 | [11 empty] | 5638
SV104 - 5639 |  |  |  | Resistor fails-short. | Dead time between alternating PWMs will be altered (maximum). 1 PWM will be permanently high, while other will be permanently low. Output of isolation transformer will not be available. No output available at HV transformer board. | iiDCE will be unable to get power from redundant HVT board, but will get power from other HVT board (in sharing with clamp board). Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Wear-out due to extensive use. Excessive humidity. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iiDCE driver board. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 10 | [9 empty] | 0 |  | 5639
SV104 - 5640 | RT1 Biasing Resistor. | R15 | To control oscillator maximum ON time. | Resistor fails-open. | Dead time between alternating PWMs will be altered (maximum). 1 PWM will be permanently high, while other will be permanently low. Output of isolation transformer will not be available. No output available at HV transformer board. | iiDCE will be unable to get power from redundant HVT board, but will get power from other HVT board (in sharing with clamp board). Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Over voltage. Over Temperature. Over stress due to shock or vibration. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iiDCE driver board. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 10 | [11 empty] | 5640
SV104 - 5641 |  |  |  | Resistor fails-short. | Dead time between alternating PWMs will be altered (maximum). 1 PWM will be permanently high, while other will be permanently low. Output of isolation transformer will not be available. No output available at HV transformer board. | iiDCE will be unable to get power from redundant HVT board, but will get power from other HVT board (in sharing with clamp board). Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Wear-out due to extensive use. Excessive humidity. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iiDCE driver board. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 10 | [11 empty] | 5641
SV104 - 5642 | Restart Timer Resistor. | R16 | To set PWM restart signal biasing. | Resistor fails-open. | Restart timer functionality will be compromised. No immediate effect on board in normal operations. | If no other failure is observed on the board, iiDCE board will stay powered. Device can operate in both monitoring and injection mode | System will keep working normally. | 1 | Over voltage. Over Temperature. Over stress due to shock or vibration. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iiDCE driver board. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [11 empty] | 5642
SV104 - 5643 |  |  |  | Resistor fails-short. | Restart timer functionality will be compromised. No immediate effect on board in normal operations. | If no other failure is observed on the board, iiDCE board will stay powered. Device can operate in both monitoring and injection mode | System will keep working normally. | 1 | Wear-out due to extensive use. Excessive humidity. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iiDCE driver board. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [11 empty] | 5643
SV104 - 5644 | Soft-Start Capacitor. | C10 | To provide soft-start biasing value. | Capacitor fails-open. | Soft start functionality will be compromised. No immediate effect on board in normal operations. | If no other failure is observed on the board, iiDCE board will stay powered. Device can operate in both monitoring and injection mode | System will keep working normally. | 1 | Mechanical stress. Localized heating for long time will separate end connection of capacitor. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iiDCE driver board. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [11 empty] | 5644
SV104 - 5645 |  |  |  | Capacitor fails-short. | PWM controller will turn off permanently. No output available for board. | iiDCE will be unable to get power from redundant HVT board, but will get power from other HVT board (in sharing with clamp board). Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Wear-out due to dielectric degradation. High-voltage transients. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iiDCE driver board. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 10 | [9 empty] | 0 |  | 5645
SV104 - 5646 | Ramp Control Resistor. | R12 | To provide ramp control of PWM. | Resistor fails-open. | PWM ramp will be affected. Output of Full Bridge circuit will be different than desired. HV transformer board will have more or less than 24 V output. | If no other failure is observed on the board, iiDCE board will stay powered. Device can operate in both monitoring and injection mode | System will keep working normally. | 1 | Over voltage. Over Temperature. Over stress due to shock or vibration. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iiDCE driver board. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [11 empty] | 5646
SV104 - 5647 |  |  |  | Resistor fails-short. | PWM ramp will be affected. Output of Full Bridge circuit will be different than desired. HV transformer board will have more or less than 24 V output. | If no other failure is observed on the board, iiDCE board will stay powered. Device can operate in both monitoring and injection mode | System will keep working normally. | 1 | Wear-out due to extensive use. Excessive humidity. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iiDCE driver board. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [9 empty] | 0 |  | 5647
SV104 - 5648 | Current Sense Signal Filtration Capacitor. | C12 | To filter the CS signal. | Capacitor fails-open. | No immediate effect. | If no other failure is observed on the board, iiDCE board will stay powered. Device can operate in both monitoring and injection mode | System will keep working normally. | 1 | Mechanical stress. Localized heating for long time will separate end connection of capacitor. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iiDCE driver board. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [11 empty] | 5648
SV104 - 5649 |  |  |  | Capacitor fails-short. | Capacitor will fail-open due to over-current. PWM current limiting functionality will be compromised while the capacitor remains shorted. No immediate effect on board in normal operations. | If no other failure is observed on the board, iiDCE board will stay powered. Device can operate in both monitoring and injection mode | System will keep working normally. | 1 | Wear-out due to dielectric degradation. High-voltage transients. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iiDCE driver board. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [9 empty] | 0 |  | 5649
SV104 - 5650 | Current Sense Capacitor. | C9 | To limit PWM current. | Capacitor fails-open. | PWM current limiting functionality will be compromised. No immediate effect on board in normal operations. | If no other failure is observed on the board, iiDCE board will stay powered. Device can operate in both monitoring and injection mode | System will keep working normally. | 1 | Mechanical stress. Localized heating for long time will separate end connection of capacitor. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iiDCE driver board. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [11 empty] | 5650
SV104 - 5651 |  |  |  | Capacitor fails-short. | PWM current limiting functionality will be compromised. No immediate effect on board in normal operations. | If no other failure is observed on the board, iiDCE board will stay powered. Device can operate in both monitoring and injection mode | System will keep working normally. | 1 | Wear-out due to dielectric degradation. High-voltage transients. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iiDCE driver board. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [9 empty] | 0 |  | 5651
SV104-12410 | Decoupling Capacitor | C11 | To Filter Noise | Capacitor fails-open. | No immediate effect on board in normal operations. | If no other failure is observed on the board, iiDCE board will stay powered. Device can operate in both monitoring and injection mode | System will keep working normally. | 1 | Mechanical stress. Localized heating for long time will separate end connection of capacitor. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iiDCE driver board. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. Vibration Testing. | None. | 5 | 5 | [11 empty] | 12410
SV104-12411 |  |  |  | Capacitor fails-short. | Internal Reference Voltage will be shorted to ground. PWM output will be disabled. Input Fuse Will be Blown No output available at HV transformer board. | iiDCE will be unable to get power from redundant HVT board, but will get power from other HVT board (in sharing with clamp board). Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Wear-out due to dielectric degradation. High-voltage transients. De-gradation of components. Water ingress during humidity condition as it is film capacitor. Overvoltage | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iiDCE driver board. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. Environmental Testing. | None. | 5 | 10 | [11 empty] | 12411
SV104-11124 | Input Filtration Capacitance | C1 | To suppress ripples on input voltage. | Capacitor fails-open. | No immediate effect on board due to presence of multiple capacitors at different stages.. | If no other failure is observed on the board, iiDCE board will stay powered. Device can operate in both monitoring and injection mode | System will keep working normally. | 1 | Mechanical stress. Localized heating for long time will separate end connection of capacitor. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iiDCE driver board. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. Vibration Testing. | None. | 5 | 5 | [11 empty] | 11124
SV104-11125 |  |  |  | Capacitor fails-short. | 15V rail will get shorted to ground thus No output available at HV transformer board . | iiDCE will be unable to get power from redundant HVT board, but will get power from other HVT board (in sharing with clamp board). Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Wear-out due to dielectric degradation. High-voltage transients. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iiDCE driver board. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 10 | [11 empty] | 11125
SV104-11126 | Current Sense Resistance | R28 | To Sense Overcurrent | Resistor fails-open. | Overcurrent Protection will be compromised during overcurrent condition at primary. No immediate Effect in normal condition. | If no other failure is observed on the board, iiDCE board will stay powered. Device can operate in both monitoring and injection mode | System will keep working normally. | 1 | Over voltage. Over Temperature. Over stress due to shock or vibration. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iiDCE driver board. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [11 empty] | 11126
SV104-11127 |  |  |  | Resistor fails-short. | IC may trigger False overcurrent and disable output. No output available at HV transformer board | iiDCE will be unable to get power from redundant HVT board, but will get power from other HVT board (in sharing with clamp board). Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | Wear-out due to extensive use. Excessive humidity. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iiDCE driver board. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [9 empty] | 0 |  | 11127
SV104 - 5652 | Output Driver Resistor. | R4,R5 | To limit gate driver current. | Resistor fails-open. | Gate driver PWM path will be broken. No output available at HV transformer board. | iiDCE will be unable to get power from redundant HVT board, but will get power from other HVT board (in sharing with clamp board). Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Over voltage. Over Temperature. Over stress due to shock or vibration. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iiDCE driver board. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 10 | [11 empty] | 5652
SV104 - 5653 |  |  |  | Resistor fails-short. | No immediate till the shorted duration. Resistor will fail-open due to over-current. Gate driver PWM path will be broken. No output available at HV transformer board. | iiDCE will be unable to get power from redundant HVT board, but will get power from other HVT board (in sharing with clamp board). Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Wear-out due to extensive use. Excessive humidity. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iiDCE driver board. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 10 | [9 empty] | 0 |  | 5653
| Full Bridge Circuit | [26 empty] | 0
SV104 - 5654 | Half Bridge Gate Driver IC. | U2, U3 | To provide gate driver signal for half bridge MOSFETs. | Both output are permanently low. | One half bridge section will not have output. Output of Full Bridge circuit will be 12 V at no load. HV transformer board will have no output as soon as load is applied. | iiDCE will be unable to get power from redundant HVT board, but will get power from other HVT board (in sharing with clamp board). Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Electrical Overstress (Overvoltage). ESD. Counterfeit part. Stress or impact during assembly. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iiDCE driver board. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 10 | [9 empty] | 0 |  | 5654
SV104 - 5655 |  |  |  | High side output is permanently low. | Full bridge functionality will be disturbed. No output will be available at HV transformer board as soon as load is applied. | iiDCE will be unable to get power from redundant HVT board, but will get power from other HVT board (in sharing with clamp board). Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Electrical Overstress (Overvoltage). ESD. Counterfeit part. Stress or impact during assembly. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iiDCE driver board. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 10 | [11 empty] | 5655
SV104 - 5656 |  |  |  | High side output is permanently high. | One MOSFET will be permanently turned ON. During times, when low side MOSFET of same half bridge will turn ON, HV DC line get shorted will ground. Due to high current flow, power MOSFETs may get damaged. Input side fuse will burn out and prevent cascading failures. | iiDCE will be unable to get power from redundant HVT board, but will get power from other HVT board (in sharing with clamp board). Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Electrical Overstress (Overvoltage). ESD. Counterfeit part. Stress or impact during assembly. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iiDCE driver board. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 10 | [9 empty] | 0 |  | 5656
SV104 - 8911 | Half Bridge Gate Driver IC. | U2, U3 | To provide gate driver signal for half bridge MOSFETs. | Low side output is permanently low. | Full bridge functionality will be disturbed. No output will be available at HV transformer board as soon as load is applied. . | iiDCE will be unable to get power from redundant HVT board, but will get power from other HVT board (in sharing with clamp board). Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Electrical Overstress (Overvoltage). ESD. Counterfeit part. Stress or impact during assembly. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iiDCE driver board. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 10 | [11 empty] | 8911
SV104 - 8912 |  |  |  | Low side output is permanently high. | During times, when high side MOSFET of same half bridge will turn ON, HV DC line get shorted with ground. Due to high current flow, power MOSFETs may get damaged. Input side fuse will burn out and prevent cascading failures. | iiDCE will be unable to get power from redundant HVT board, but will get power from other HVT board (in sharing with clamp board). Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Electrical Overstress (Overvoltage). ESD. Counterfeit part. Stress or impact during assembly. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iiDCE driver board. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 10 | [11 empty] | 8912
SV104 - 8913 |  |  |  | Both outputs are permanently high. | Both MOSFETs will be permanently turned ON. HV DC line will get shorted with ground. Due to high current flow, power MOSFETs may get damaged. Input side fuse will burn out and prevent cascading failures. | iiDCE will be unable to get power from redundant HVT board, but will get power from other HVT board (in sharing with clamp board). Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Electrical Overstress (Overvoltage). ESD. Counterfeit part. Stress or impact during assembly. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iiDCE driver board. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 10 | [11 empty] | 8913
SV104 - 5657 | Half Bridge Gate Driver IC - Filter Capacitor. | C4,C5 | To provide high side gate driver floating supply. | Capacitor fails-open. | Output of gate driver IC will be affected. No output available at HV transformer board. | iiDCE will be unable to get power from redundant HVT board, but will get power from other HVT board (in sharing with clamp board). Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Mechanical stress. Localized heating for long time will separate end connection of capacitor. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iiDCE driver board. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 10 | [11 empty] | 5657
SV104 - 5658 |  |  |  | Capacitor fails-short. | Output of gate driver IC will be affected. No output available at HV transformer board. | iiDCE will be unable to get power from redundant HVT board, but will get power from other HVT board (in sharing with clamp board). Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Wear-out due to dielectric degradation. High-voltage transients. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iiDCE driver board. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 10 | [9 empty] | 0 |  | 5658
SV104 - 5659 | Gate Driver Output Circuit - Resistor. | R7,R24,R6,R23 | To provide path between gate driver IC and gate. | Resistor fails-open. | Output path of gate driver IC will be broken for one MOSFET. Distorted square wave will be available at full bridge circuit output. HV transformer board will have lesser output than desired. | If no other failure is observed on the board, iiDCE board will stay powered. Device can operate in both monitoring and injection mode | System will keep working normally. | 1 | Over voltage. Over Temperature. Over stress due to shock or vibration. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iiDCE driver board. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [11 empty] | 5659
SV104 - 5660 |  |  |  | Resistor fails-short. | Over-current will cause the resistor to eventually fail-open. Output path of gate driver IC will be broken for one MOSFET. Distorted square wave will be available at full bridge circuit output. HV transformer board will have lesser output than desired. | If no other failure is observed on the board, iiDCE board will stay powered. Device can operate in both monitoring and injection mode | System will keep working normally. | 1 | Wear-out due to extensive use. Excessive humidity. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iiDCE driver board. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [11 empty] | 5660
SV104 - 5661 | Gate Driver Output Circuit - General Purpose Diode. | D1,D2,D3,D4 | To turn off the MOSFET quickly through low resistance path at gate. | Diode fails-open. | MOSFET will turn off through larger resistor which will result in increased switching losses. No immediate effect in case of normal operations. | If no other failure is observed on the board, iiDCE board will stay powered. Device can operate in both monitoring and injection mode | System will keep working normally. | 1 | Excessive forward current flow. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iiDCE driver board. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [11 empty] | 5661
SV104 - 5662 |  |  |  | Diode fail-short. | Over-current will cause the diode to eventually fail-open. MOSFET will turn off through larger resistor which will result in increased switching losses. No immediate effect in case of normal operations. | If no other failure is observed on the board, iiDCE board will stay powered. Device can operate in both monitoring and injection mode | System will keep working normally. | 1 | Large reverse voltage. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iiDCE driver board. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [11 empty] | 5662
SV104-11128 | Gate Driver Output Circuit -Discharge Resistor. | R2,R3,R20,R21 | To provide low resistance path between gate driver IC and gate to discharge gate capacitance. | Resistor fails-open. | Gate Capacitance will discharge slowly through high resistance path thus on/off time will be disturbed Switching losses will increase. No immediate effect ion board. | If no other failure is observed on the board, iiDCE board will stay powered. Device can operate in both monitoring and injection mode | System will keep working normally. | 1 | Over voltage. Over Temperature. Over stress due to shock or vibration. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iiDCE driver board. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [11 empty] | 11128
SV104-11129 |  |  |  | Resistor fails-short. | Switching losses will increase. No immediate effect on board. | If no other failure is observed on the board, iiDCE board will stay powered. Device can operate in both monitoring and injection mode | System will keep working normally. | 1 | Wear-out due to extensive use. Excessive humidity. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iiDCE driver board. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [11 empty] | 11129
SV104-11130 | MOSFET resistance for Miller Capacitance | R10,R27,R11,R26 | To discharge capacitance between all terminals of MOSFET | Resistor fails-open | Abnormal Behavior of MOSFET Might turn ON/OFF abnormally and can damage board. No output available at HV transformer board | iiDCE will be unable to get power from redundant HVT board, but will get power from other HVT board (in sharing with clamp board). Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Over voltage. Over Temperature. Over stress due to shock or vibration. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iiDCE driver board. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. Vibration testing. | None. | 5 | 10 | [11 empty] | 11130
SV104-11131 |  |  |  | Resistor fails-short | Gate and Source of MOSFET will have no voltage difference so MOSFET cannot operate No output available at HV transformer board | iiDCE will be unable to get power from redundant HVT board, but will get power from other HVT board (in sharing with clamp board). Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Wear-out due to extensive use. Excessive humidity. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iiDCE driver board. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. Vibration testing. | None. | 5 | 10 | [11 empty] | 11131
SV104-11132 | Half Bridge Gate Driver IC - High Side Supply Capacitor. | C7,C15,C16,C8 | To provide high side supply and to ensure bootstrapping in order to operate MOSFET. | One Capacitor fails-open. | No immediate effect as the parallel capacitor will be available and will make sure that MOSFET works properly | If no other failure is observed on the board, iiDCE board will stay powered. Device can operate in both monitoring and injection mode | System will keep working normally. | 1 | Mechanical stress. Localized heating for long time will separate end connection of capacitor. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iiDCE driver board. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [11 empty] | 11132
SV104-11133 |  |  |  | Both Capacitors fails-open. | MOSFET Cannot operate properly No output available at HV transformer board | iiDCE will be unable to get power from redundant HVT board, but will get power from other HVT board (in sharing with clamp board). Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Mechanical stress. Localized heating for long time will separate end connection of capacitor. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iiDCE driver board. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 10 | [11 empty] | 11133
SV104-11134 |  |  |  | Capacitor fails-short. | MOSFET Cannot operate properly IC may get damaged No output available at HV transformer board | iiDCE will be unable to get power from redundant HVT board, but will get power from other HVT board (in sharing with clamp board). Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Wear-out due to dielectric degradation. High-voltage transients. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iiDCE driver board. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 10 | [11 empty] | 11134
SV104 - 5663 | Full Bridge Circuit - MOSFET | Q1,Q2,Q3,Q4 | To convert HV DC to HV AC signal. | MOSFET fails-open. | Distorted square wave will be available at full bridge circuit output. HV transformer board will have lesser output than desired. | If no other failure is observed on the board, iiDCE board will stay powered. Device can operate in both monitoring and injection mode | System will keep working normally. | 1 | Overheating Mechanical stress resulting in cracked MOSFET body. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iiDCE driver board. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [11 empty] | 5663
SV104 - 5664 |  |  |  | MOSFET fails-short. | No voltage will be available at transformer output, for the shorted duration. No output available at HV transformer board. | iiDCE will be unable to get power from redundant HVT board, but will get power from other HVT board (in sharing with clamp board). Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Transients Overheating as a result of loose connection with heat sink Overcurrent Counterfeit part Damage during mechanical assembly of board Metallic debris stuck in between terminals | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iiDCE driver board. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 10 | [11 empty] | 5664
SV104-11135 | Gate Driver Output Circuit -Pull Down resistance. | R29,R8 | To provide current sense signal to controller | One Resistor fails-open. | Current over limit value will decrease down to half. No immediate affect in normal condition but in case of overloaded condition current limit will be activated early. | If no other failure is observed on the board, iiDCE board will stay powered. Device can operate in both monitoring and injection mode | System will keep working normally. | 1 | Over voltage. Over Temperature. Over stress due to shock or vibration. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iiDCE driver board. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [9 empty] | 0 |  | 11135
SV104-11136 |  |  |  | Both Resistor fails-open. | Full bridge circuit ground connection will be disconnected No output available at HV transformer board | iiDCE will be unable to get power from redundant HVT board, but will get power from other HVT board (in sharing with clamp board). Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Over voltage. Over Temperature. Over stress due to shock or vibration. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iiDCE driver board. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 10 | [11 empty] | 11136
SV104-11137 |  |  |  | Resistor fails-short. | No immediate effect in case of normal operations. Overcurrent protection will not be available. | If no other failure is observed on the board, iiDCE board will stay powered. Device can operate in both monitoring and injection mode | System will keep working normally. | 1 | Wear-out due to extensive use. Excessive humidity. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iiDCE driver board. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [11 empty] | 11137
SV104 - 5665 | HV Isolation Transformer | P113720 | To step down 400 V AC to 24 V AC. | Primary winding fails-open. | No voltage will be available at transformer output. No output available at HV transformer board. | iiDCE will be unable to get power from redundant HVT board, but will get power from other HVT board (in sharing with clamp board). Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | High operating temperature. Overloading. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iiDCE driver board. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 10 | [11 empty] | 5665
SV104 - 5666 |  |  |  | Secondary winding fails-open. | No output will be available at HV transformer board. | iiDCE will be unable to get power from redundant HVT board, but will get power from other HVT board (in sharing with clamp board). Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | High operating temperature. Overloading. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iiDCE driver board. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 10 | [11 empty] | 5666
SV104 - 5667 |  |  |  | Core degradation. | Output voltage will be less than desired value. | If no other failure is observed on the board, iiDCE board will stay powered. Device can operate in both monitoring and injection mode | System will keep working normally. | 1 | Mechanical Stress | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iiDCE driver board. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [11 empty] | 5667
SV104 - 5668 |  |  |  | Winding insulation melting. | Turn ratio of transformer will be affected. Output voltage will be less than desired value. | If no other failure is observed on the board, iiDCE board will stay powered. Device can operate in both monitoring and injection mode | System will keep working normally. | 1 | Over voltage. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iiDCE driver board. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [11 empty] | 5668
SV104 - 7007 |  |  |  | Isolation Failure. | If failure is such that board cannot provide any level of isolation then it will damage iiDCE board. iiDCE board will not be powered up. | Controls and communication will not be available. If the device was in injection mode it will switch to monitoring mode. | Affected device and associated group will not be able to enter injection mode. System will keep working normally with reduced injection capability. | 5 | Temperature cycling. Manufacturing Deficiency. Vibration. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iiDCE driver board. | 1 | 5 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 25 | [11 empty] | 7007
SV104 - 7008 |  |  |  | Auxiliary winding failure(Open) | No auxiliary voltage will be available. Startup circuit will not shutdown eventually burn out. No output will be available for HV-ISO board | iiDCE will be unable to get power from redundant HVT board, but will get power from other HVT board (in sharing with clamp board). Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | Over voltage. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iiDCE driver board. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [9 empty] | 0 |  | 7008
SV104 - 7009 |  |  |  | Post insulator fails | Insulator failure will not have impact during normal condition as it is to prevent early partial discharge during humid condition. This will not impact bypass side board in any condition | iiDCE will be unable to get power from redundant HVT board, but will get power from other HVT board (in sharing with clamp board). Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Corrosion. Manufacturing Deficiency. Vibration. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iiDCE driver board. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 10 | [9 empty] | 0 |  | 7009
SV104 - 7010 |  |  |  | Potting crack or physical damage | Partial discharge will start resulting in degradation of isolation barrier with the time. No immediate effect as will not be critical as isolation of even 400 Vrms will be enough. | If no other failure is observed on the board, iiDCE board will stay powered. Device can operate in both monitoring and injection mode | System will keep working normally. | 2 | Manufacturing Deficiency. Vibration. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iiDCE driver board. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 10 | [11 empty] | 7010
SV104 - 5669 | HV Isolation Transformer - output Side Full Rectifier - Diode | D5,D6,D8 | To convert 24 V AC to 24 V DC. | Diode fails-open. | Output cut to half if half side is working. | iiDCE will be unable to get power from redundant HVT board, but will get power from other HVT board (in sharing with clamp board). Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Excessive forward current flow. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iiDCE driver board. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 10 | [11 empty] | 5669
SV104 - 5670 |  |  |  | Diode fails-short. | Secondary winding will get shorted if any diode fails-short. As a result of shortage, excessive amount of current will flow damaging two diodes permanently. Diodes will eventually get open and no output will be available | iiDCE will be unable to get power from redundant HVT board, but will get power from other HVT board (in sharing with clamp board). Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Large reverse voltage. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iiDCE driver board. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 10 | [11 empty] | 5670
SV104 - 5229 | Output Side Capacitor. | C13,C14 | To suppress output side ripples and to provide filtration. | Capacitor fails-open. | Output voltage may have ripples. No immediate effect on HV transformer board output. | If no other failure is observed on the board, iiDCE board will stay powered. Device can operate in both monitoring and injection mode | System will keep working normally. | 1 | Mechanical stress. Localized heating for long time will separate end connection of capacitor. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iiDCE driver board. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [11 empty] | 5229
SV104 - 5230 |  |  |  | Capacitor fails-short. | No voltage available at the output for the shorted duration. | iiDCE will be unable to get power from redundant HVT board, but will get power from other HVT board (in sharing with clamp board). Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Wear-out due to dielectric degradation. High-voltage transients. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iiDCE driver board. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 10 | [11 empty] | 5230
SV104 - 5671 | HV Isolation Transformer - Feedback Side Full Rectifier - Diode | D15,D16,D19,D20 | To convert 24 V AC to 24 V DC for feedback. | Diode fails-open. | Output cut to half if half side is working. | iiDCE will be unable to get power from redundant HVT board, but will get power from other HVT board (in sharing with clamp board). Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Excessive forward current flow. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iiDCE driver board. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 10 | [11 empty] | 5671
SV104 - 5672 |  |  |  | Diode fails-short. | Auxiliary winding will get shorted if any diode fails-short. As a result of shortage, excessive amount of current will flow damaging two diodes permanently. Diodes will eventually get open and no output will be available. | iiDCE will be unable to get power from redundant HVT board, but will get power from other HVT board (in sharing with clamp board). Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Large reverse voltage. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iiDCE driver board. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 10 | [11 empty] | 5672
SV104 - 5673 | Output Side Capacitor. | C17,C18 | To suppress output side ripples and to provide filtration. | Capacitor fails-open. | Output voltage may have ripples. No immediate effect on HV transformer board output. | If no other failure is observed on the board, iiDCE board will stay powered. Device can operate in both monitoring and injection mode | System will keep working normally. | 1 | Mechanical stress. Localized heating for long time will separate end connection of capacitor. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iiDCE driver board. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [11 empty] | 5673
SV104 - 5674 |  |  |  | Capacitor fails-short. | No voltage available at the output for the shorted duration. | iiDCE will be unable to get power from redundant HVT board, but will get power from other HVT board (in sharing with clamp board). Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Wear-out due to dielectric degradation. High-voltage transients. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iiDCE driver board. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 10 | [11 empty] | 5674
SV104-11138 | Current Limiting resistance for LED (D9) | R44 | To limit current through the LED (D9) | Resistor fails-open | LED indication functionality will be compromised No immediate effect on HV transformer board output. | If no other failure is observed on the board, iiDCE board will stay powered. Device can operate in both monitoring and injection mode | System will keep working normally. | 1 | Over voltage. Over Temperature. Over stress due to shock or vibration. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iiDCE driver board. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. Vibration testing. | None. | 5 | 5 | [11 empty] | 11138
SV104-11139 |  |  |  | Resistor fails-short | LED indication functionality will be compromised No immediate effect on HV transformer board output. | If no other failure is observed on the board, iiDCE board will stay powered. Device can operate in both monitoring and injection mode | System will keep working normally. | 1 | Wear-out due to extensive use. Excessive humidity. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iiDCE driver board. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. Vibration testing. | None. | 5 | 5 | [11 empty] | 11139
SV104-11140 | LED for status indication of voltage produced | D9 | Visual indication for board output status | Diode fails-open | LED indication functionality will be compromised No immediate effect on HV transformer board output. | If no other failure is observed on the board, iiDCE board will stay powered. Device can operate in both monitoring and injection mode | System will keep working normally. | 1 | Over voltage. Over Temperature. Over stress due to shock or vibration. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iiDCE driver board. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. Vibration testing. | None. | 5 | 5 | [11 empty] | 11140
SV104-11141 |  |  |  | Diode fails-short. | LED indication functionality will be compromised No immediate effect on HV transformer board output. | If no other failure is observed on the board, iiDCE board will stay powered. Device can operate in both monitoring and injection mode | System will keep working normally. | 1 | Wear-out due to extensive use. Excessive humidity. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iiDCE driver board. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. Vibration testing. | None. | 5 | 5 | [11 empty] | 11141
SV104-11142 | Load at output | R42,R43 | To keep open load voltage within a range | Resistor fails-open | No immediate effect on board. | If no other failure is observed on the board, iiDCE board will stay powered. Device can operate in both monitoring and injection mode | System will keep working normally. | 1 | Over voltage. Over Temperature. Over stress due to shock or vibration. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iiDCE driver board. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. Vibration testing. | None. | 5 | 5 | [11 empty] | 11142
SV104-11143 |  |  |  | Resistor fails-short | 24V supply will be shorted out to ground. Resistance will eventually fail open due to over current. No output available at HV transformer board | iiDCE will be unable to get power from redundant HVT board, but will get power from other HVT board (in sharing with clamp board). Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Wear-out due to extensive use. Excessive humidity. De-gradation of components. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iiDCE driver board. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. Vibration testing. | None. | 5 | 10 | [11 empty] | 11143
SV104 - 5675 | Heat Sink | HS1,HS2,HS3,HS4,HS5,HS6,HS7,HS8. | To provide cooling functionality for power components. | Loose connection between heat sink and power component. | Affected component will face high temperature rise during nominal current operations. Power component may get damaged causing HV transformer board output voltage to drop. | iiDCE will be unable to get power from redundant HVT board, but will get power from other HVT board (in sharing with clamp board). Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | External overstress. Mis-handling. Excessive temperature causing joint melts. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iiDCE driver board. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 10 | [11 empty] | 5675
SV104-11451 | Secondary Winding Connector | J2 | Secondary of transformer | Connector Disconnected by external Force. | Secondary winding will be opened. No output available at HV transformer board. | iiDCE will be unable to get power from redundant HVT board, but will get power from other HVT board (in sharing with clamp board). Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Open Connections due to vibrations, mis-handling or mechanical stress. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. Vibration Testing. | None. | 5 | 10 | [11 empty] | 11451
SV104-11452 |  |  |  | Connector Burned out | Due to sparking connector will heat up and eventually burnout No output available at HV transformer board. | iiDCE will be unable to get power from redundant HVT board, but will get power from other HVT board (in sharing with clamp board). Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Connection Loose or Sparking at terminals Open Connections due to vibrations, mis-handling or mechanical stress. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. Vibration Testing. | None. | 5 | 10 | [11 empty] | 11452
SV104-11453 | Low voltage DC output Connector | J4 | Output of HVT board | Connector Disconnected by external Force. | Output path will be broken. No output available at HV transformer board. | iiDCE will be unable to get power from redundant HVT board, but will get power from other HVT board (in sharing with clamp board). Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Open Connections due to vibrations, mis-handling or mechanical stress. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. Vibration Testing. | None. | 5 | 10 | [11 empty] | 11453
SV104-11454 |  |  |  | Connector Burned out | Due to sparking connector will heat up and eventually burnout Output path will be broken. No output available at HV transformer board. | iiDCE will be unable to get power from redundant HVT board, but will get power from other HVT board (in sharing with clamp board). Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Connection Loose or Sparking at terminals Open Connections due to vibrations, mis-handling or mechanical stress. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. Vibration Testing. | None. | 5 | 10 | [11 empty] | 11454
SV104-11455 | Auxiliary winding Connector | J6 | Auxiliary winding of transformer for 24AUX | Connector Disconnected by external Force. | 24AUX path will be broken. Startup circuitry will turn on permanently resulting in overheating and permanently damage to startup resistor. No output available once HV-ISO reboot. | iiDCE will be unable to get power from redundant HVT board, but will get power from other HVT board (in sharing with clamp board). Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Open Connections due to vibrations, mis-handling or mechanical stress. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. Vibration Testing. | None. | 5 | 10 | [11 empty] | 11455
SV104-11456 |  |  |  | Connector Burned out | Due to sparking connector will heat up and eventually burnout 24AUX path will be broken. Startup circuitry will turn on permanently resulting in overheating and permanently damage to startup resistor. No output available once HV-ISO reboot. | iiDCE will be unable to get power from redundant HVT board, but will get power from other HVT board (in sharing with clamp board). Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Connection Loose or Sparking at terminals Open Connections due to vibrations, mis-handling or mechanical stress. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. Vibration Testing. | None. | 5 | 10 | [11 empty] | 11456
SV104-11457 | Primary winding of transformer | J1,J5 | primary winding of transformer | Connector Disconnected by external Force. | No voltage will be available at transformer output. No output available at HV transformer board. | iiDCE will be unable to get power from redundant HVT board, but will get power from other HVT board (in sharing with clamp board). Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Open Connections due to vibrations, mis-handling or mechanical stress. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. Vibration Testing. | None. | 5 | 10 | [11 empty] | 11457
SV104-11458 |  |  |  | Connector Burned out | Due to sparking connector will heat up and eventually burnout No voltage will be available at transformer output. No output available at HV transformer board. | iiDCE will be unable to get power from redundant HVT board, but will get power from other HVT board (in sharing with clamp board). Device can operate in both monitoring and injection mode. | System will keep working normally. | 2 | Connection Loose or Sparking at terminals Open Connections due to vibrations, mis-handling or mechanical stress. De-gradation of components. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. | 1 | 2 | HALT. Electrical Stress Testing. Thermal Stress Testing. Vibration Testing. | None. | 5 | 10 | [11 empty] | 11458
SV104 - 7011 | Connector failure | J3 | To provide input supply | Connector disconnected by external force | No output available at HV transformer board. Redundant power to one of the iiDCE board will be cut-off. | iiDCE will be unable to get power from redundant HVT board, but will get power from other HVT board (in sharing with clamp board). Device can operate in both monitoring and injection mode. | System will keep working normally. | 1 | External overstress. Mis-handling. Excessive temperature causing joint melts. | Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Redundant HV Transformer board to power-up iiDCE driver board. | 1 | 1 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 5 | [11 empty] | 7011
SV104 - 7012 |  |  |  | Connector shorted | PHT-DC board external capacitor will dump full energy in board. HV-ISO board's input traces will burn out. Board will be damaged permanently. | Controls and communication will not be available. If the device was in injection mode it will switch to monitoring mode. | Affected device and associated group will not be able to enter injection mode. System will keep working normally with reduced injection capability. | 4 | Manufacturing Deficiency. Excessive temperature causing joint melts. Excessive humidity. | Usage of over-rated components. Using components with industrial grade scale. Choosing components with enough FIT rate to fulfil the product life requirements. Conformal coating whole connector and mask only mating part of pins. | 1 | 4 | HALT. Electrical Stress Testing. Thermal Stress Testing. | None. | 5 | 20 | [11 empty] | 7012
0

## Data Validation (hidden)
Status
Approved
Review Pending
Reviewed by QA