## Title
Title: | SmartValve 10-1800 v1.04 - SCRD Gate Driver Board Rev2 (P112269 / P112262) - Potential Failure Mode Effects and Criticality Analysis (Design FMECA)
Project: | SmartValve 10-1800 v1.04
PS19 QPI | PS19 Technical Experts | Smart Wires Reviewer
Azeem, Talha, Arslan | Haris, Abdul Qadeer, Noman Akbar | Dr. Shilei

## Revision History
Revision History
Date | Version | Description
2021-02-17 | 1 | Initial draft based on Rev0. schematic.
2021-09-14 | 1.1 | Updated FMECA based on the Rev1 schematic done by PS19 QPI team.
2022-01-14 | 1.2 | Updated FMECA based on the Rev2 schematic done by PS19 QPI team.
2022-02-02 | 1.3 | Reviewed and updated by PS19 Hardware team for the changes done based on the Rev2 schematic
2022-02-07 | 1.4 | Updated the FMECA based on the feedback received from PS19 Hardware team for the improvements by PS19 QPI team.
2022-11-21 | 1.5 | Updated the FMECA based on the feedback received from PS19 Hardware team for the improvements by PS19 QPI team.
2023-03-30 | 1.6 | Updated the FMECA based on the feedback received from PS19 Hardware team for the improvements by PS19 QPI team based on Rev2 schematics.
2023-09-27 | 1.7 | Updated the FMECA based on the feedback received from SmartWires team for the improvements by PS19 QPI team based on Rev2 schematics.
2024-06-12 | 1.8 | Updated the FMECA Alarms and Telemetry by PS19 QPI team based on Rev2 schematics.

## Definitions-Terms
Definitions / Terms / Acronyms
Term | Description | Term | Description
A-K | Anode-to-Cathode | LCB | Liquid Cooling Block
BF | Bypass Filter | PHT | Power Harvesting Transformer
CTP | Current Transformer for Power | ETP | Electrical Test Procedure
DCCT | DC current transducer | IP | Intrusion Protection
DCE | Digital Computational Engine | MES | Manufacturing Execution System
EFT | Electrical Fast Transient | CTQ | Critical To Quality
EMS | Energy Management System
EOL | End Of Line
FCS | Fault Current Sensor
FO | Fiber Optic
FR | Flame Retardant
G-K | Gate-to-Cathode
HALT | Highly-Accelerated Life Testing
HASS | High accelerated stress screening
HCT | High Current Testing
LCB | Liquid Cooling Block
LCS | Line Current Sensor
OVP | Over-Voltage Protection
PCB | Printed Circuit Board
PIB | Power Interface Board
PLM | PowerLine Manager
PSB | Power Supply Board
RF | Radio Frequency
RTU | Remote Terminal Unit
SB | Smart Bypass
SCR | Silicon Controlled Rectifier
SI | Smart Interface
SMD | Surface Mounted Device
SV | Smart Valve
SVC | SmartValve Controller
VPI | Vacuum Pressure Impregnation
VSL | Vacuum Series Link
UPSB | Universal Power Supply Board
TBR | To be Reviewed

## Design-Traceability
Design Traceability
Sr. | Design Artifact | Rev | Link
1 | SmartValve 10-1800 v1.04 - Wiring Drawing - Bypass, MVAr Section Harnesses Diagram, PHT Shorting and Capacitor Voltage Measurement Blocks | 4 | Box Link
2 | SmartValve 10-1800 v1.04 - Wiring Drawing - Power Supply Scheme Gen2-v2-FAI | v2 | Box Link
3 | SmartValve 10-1800 v1.04 - PCBAs - iSCR Driver Board Functional Block Diagram | 2 | Box Link
4 | SmartValve 10-1800 v1.04 - PCBAs - iSCR Driver Board Schematic | 2 | Box Link
5 | SmartValve 10-1800 v1.04 - PCBAs - iSCR Driver Board Design Document | A | Box Link

## Scores
|  | Risk Factor (S x O) Scores | [5 empty] | SmartValve v1.04 Risk Factor (S x O) Counts
Occurrence | 5 | 5 | 10 | 15 | 20 | 25 | Occurrence | 5 | 0 | 0 | 0 | 0 | 0
| 4 | 4 | 8 | 12 | 16 | 20 |  | 4 | 0 | 0 | 0 | 0 | 0
| 3 | 3 | 6 | 9 | 12 | 15 |  | 3 | 0 | 0 | 0 | 0 | 0
| 2 | 2 | 4 | 6 | 8 | 10 |  | 2 | 15 | 16 | 96 | 16 | 0
| 1 | 1 | 2 | 3 | 4 | 5 |  | 1 | 94 | 44 | 90 | 7 | 0
|  | 1 | 2 | 3 | 4 | 5 |  |  | 1 | 2 | 3 | 4 | 5
|  | Severity | [6 empty] | Severity
[9 empty] | Total risks: |  |  |  | 378
[9 empty] | Total risks require mitigation based on S x O: |  |  |  | 16
| Risk Priority Number (S x O x D) Scores | [6 empty] | SmartValve v1.04 RPN (S x O x D) Counts
Severity x Occurrence (S x O) | 25 | 25 | 50 | 75 | 100 | 125 | Severity x Occurrence (S x O) | 25 | 0 | 0 | 0 | 0 | 0
| 24 | 24 | 48 | 72 | 96 | 120 |  | 24 | 0 | 0 | 0 | 0 | 0
| 23 | 23 | 46 | 69 | 92 | 115 |  | 23 | 0 | 0 | 0 | 0 | 0
| 22 | 22 | 44 | 66 | 88 | 110 |  | 22 | 0 | 0 | 0 | 0 | 0
| 21 | 21 | 42 | 63 | 84 | 105 |  | 21 | 0 | 0 | 0 | 0 | 0
| 20 | 20 | 40 | 60 | 80 | 100 |  | 20 | 0 | 0 | 0 | 0 | 0
| 19 | 19 | 38 | 57 | 76 | 95 |  | 19 | 0 | 0 | 0 | 0 | 0
| 18 | 18 | 36 | 54 | 72 | 90 |  | 18 | 0 | 0 | 0 | 0 | 0
| 17 | 17 | 34 | 51 | 68 | 85 |  | 17 | 0 | 0 | 0 | 0 | 0
| 16 | 16 | 32 | 48 | 64 | 80 |  | 16 | 0 | 0 | 0 | 0 | 0
| 15 | 15 | 30 | 45 | 60 | 75 |  | 15 | 0 | 0 | 0 | 0 | 0
| 14 | 14 | 28 | 42 | 56 | 70 |  | 14 | 0 | 0 | 0 | 0 | 0
| 13 | 13 | 26 | 39 | 52 | 65 |  | 13 | 0 | 0 | 0 | 0 | 0
| 12 | 12 | 24 | 36 | 48 | 60 |  | 12 | 0 | 0 | 0 | 0 | 0
| 11 | 11 | 22 | 33 | 44 | 55 |  | 11 | 0 | 0 | 0 | 0 | 0
| 10 | 10 | 20 | 30 | 40 | 50 |  | 10 | 0 | 0 | 0 | 0 | 0
| 9 | 9 | 18 | 27 | 36 | 45 |  | 9 | 0 | 0 | 0 | 0 | 0
| 8 | 8 | 16 | 24 | 32 | 40 |  | 8 | 3 | 12 | 1 | 0 | 0
| 7 | 7 | 14 | 21 | 28 | 35 |  | 7 | 0 | 0 | 0 | 0 | 0
| 6 | 6 | 12 | 18 | 24 | 30 |  | 6 | 0 | 9 | 63 | 1 | 23
| 5 | 5 | 10 | 15 | 20 | 25 |  | 5 | 0 | 0 | 0 | 0 | 0
| 4 | 4 | 8 | 12 | 16 | 20 |  | 4 | 8 | 0 | 1 | 0 | 14
| 3 | 3 | 6 | 9 | 12 | 15 |  | 3 | 2 | 4 | 37 | 5 | 42
| 2 | 2 | 4 | 6 | 8 | 10 |  | 2 | 8 | 0 | 1 | 0 | 49
| 1 | 1 | 2 | 3 | 4 | 5 |  | 1 | 1 | 0 | 3 | 0 | 91
|  | 1 | 2 | 3 | 4 | 5 |  |  | 1 | 2 | 3 | 4 | 5
|  | Detection | [6 empty] | Detection
[8 empty] | Total risks: |  |  |  |  | 378
[8 empty] | Total risks require mitigation based on S x O x D: |  |  |  |  | 0

## S-O-D Definitions
Severity, or Consequence Evaluation Criteria: Worst Case Evaluation of Failure Mode |  |  |  | Occurrence: Probability of occurrence within the product life based on the design as is exists today
Score | Criteria | Notes | Example | Score | Notes | Probability Description | Probability
5 | Failure causes death or causes transmission line open circuit, full or partial fault protection compromised. | Extremely hazardous failure, threatening to business continuity. | Fault detection mechanism failure . IGBT shorting the capacitor bank. Power to one or more SCR driver boards discontinued while unit is in injection mode. Mechanical failure causing line to open. | 5 | Very high probability | 1 in 10 or greater | 0.1 ≤ Po
4 | Failure causes severe injury to personnel requiring hospitalization, severe property damage such as damage to a structure, transmission line damage, major damage to system other than transmission line requiring immediate interruption of line service, loss of control of SmartValve v1.04 when in Injection Mode, device is forced to monitoring mode, with reduced fault protection (i.e. redundancy compromised). | Highly hazardous failure, threatening to business reputation. | iiDCE RF communication loss in injection mode. iiDCE losing control of SCRs. | 4 | High probability | 1 in 100 or greater | 0.01 ≤ Po < 0.1
3 | Failure causes minor injury to personnel requiring out-patient treatment, moderate property damage not involving a structure, moderate system damage other than transmission line that requires future interruption of line service to repair, loss of control of SmartValve v1.04 when in Monitoring Mode, device is forced to monitoring mode with full fault protection available. | Moderately hazardous failure, threatening to product reputation. | iiDCE RF communication loss in monitoring mode. Any control boards' failure, forcing device to monitoring mode. Mechanical failure causing enclosure temperature to rise, forcing device to stay in monitoring mode. | 3 | Moderate probability | 1 in 1,000 or greater | 0.001 ≤ Po < 0.01
2 | Failure causes minor property damage, minor system damage other than primary conductor or loss of SmartValve v1.04 such as loss of performance, unit forced into Monitoring Mode, or significant impact on unit life | Minor hazard, minor consequence. | Rise in on-board power losses, impacting components' life, Clamp board feedback not available. | 2 | Low probability | 1 in 10,000 or greater | 0.0001 ≤ Po < 0.001
1 | Failure causes unscheduled maintenance, no immediate loss of performance. | No hazard. | On-board noise filtration compromised. One of many bolts failure. | 1 | Remote probability | Less than 1 in 10,000 | Po < 0.0001
Detection: Likelihood of failure mode detection by design | [5 empty] | Target product life for the purposes of this FMECA is 40 years.
Score | Description | Criteria | Definition
5 | Very remote probability to absolute uncertainty of detection | Design will not and/or cannot detect the potential cause/mechanism or subsequent failure mode, or the likelihood of detection is very remote. | PD < 0.1 | RPN Conditions | Color
4 | Very low to remote probability of detection | Design has a very low to remote likelihood of detecting the potential cause/mechanism or subsequent failure mode. | 0.1 ≤ PD < 0.5 | Value ≥ 70
3 | Moderate to low probability of detection | Design has a moderate to low likelihood of detecting the potential cause/mechanism or subsequent failure mode. | 0.5 ≤ PD < 0.95 | 70 > Value ≥ 60
2 | High to moderately high probability of detection | Design has a high to moderately high likelihood of detecting the potential cause/mechanism or subsequent failure mode. | 0.95 ≤ PD < 0.995 | 60 > Value ≥ 50
1 | Almost certain to very high probability of detection | Design has an almost certain chance of detecting the potential cause/mechanism or subsequent failure mode or the likelihood of detection is very high. | 0.995 ≤ PD | Value < 50
Review Status
Approved
Reviewed by QA
Review Pending

## Lookup_Table
Old Nomenclature | New Nomenclature | Description
iiSC | CC | Convertor Controller
iiGD | IMD | IGBT Module Driver
iiDCE | SVMC | SmartValve Master Controller
UPSB | MPS | Multi-Port Power Supply
iSCR | SCRD-F | SCR Drive – Follower
PHT-DC-PSB | PHTR | PHT Rectifier
iVSL | VSLD | Vacuum Switch Link Drive
iClamp | Clamp | Clamp
HV-Iso Board (Rectifier) | IPSR | PCBA, Isolation Power Supply Rectifier
HV-Iso Board (Input side) | IPSI | PCBA, Isolation Power Supply Inverter
Note: 10-1800 has old nomenclature, whereas in 10-3600, new nomenclature will be used

## DFMECA
ID. | Component | Reference Designator | Functional Requirement | Potential Failure Mode | Potential Effect(s) of Failure |  |  | Severity Score | Potential Causes / Triggers of Failure | Failure Safeguards | Occurrence Score | S x O | Existing Conditions |  |  | RPN (S x O x D) | Telemetry | Alert Message | Recommended Action(s) / Remarks | Comments from Reviewer | Target Completion Date | Action Results |  |  |  |  | Status
[5 empty] | Local - Effect at the sub assembly or component level | Higher Level - Effect at SmartValve v1.04 | End - Effect at System Level | [5 empty] | Verification & Validation Method | Detection Method | Detection Score | [6 empty] | Actions Taken | Severity Score | Occurrence Score | Detection Score | New RPN
| SCRD Gate Driver Board Rev2 (P112269 / P112262) | [26 empty] | 0
| SCRD Gate Driver Board - Power Supply Section | [26 empty] | 0
SV104-1305 | Input Power Connectors. | CONN1, CONN2 | Provide power to onboard electronics. | Power not available from both input connectors. | No power to the affected SCR gate driver board. Fault-current handling not available in one direction. Device will be unable to initiate the trigger for all SCRs in one direction when moving from injection mode to monitoring mode and vice-versa, | During mode transition, no SCR will be handling the line current in one direction. IGBTs may get damaged in case of surge current event, if loss of SCRs occurs in injection mode. Device's default behavior will be to disallow injection mode operation. The device is capable of injection, however, and end user may request to override this protection. | Affected device and its associated group of devices will transit to monitoring mode. System will keep working with reduced injection capability. | 4 | Vibration. Improper bend radius during assembly. PSB connectivity failure from SCR. | Connectors with secure contact mating. | 2 | 8 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | On board SCR gate current measurement. | 1 | 8 | In Bypass Telemetry field 'SCR and Clamp Board Status' will show following: Cable break detected | On SmartInterface following Alarm will be raised: SCR Driver Board Malfunctioning | If the SCR gate measurement circuits detect this, injection mode shall not be allowed as the IGBTs will be unprotected from fault currents in the affected direction. | SJ: No Comment AI: we do not need the SCRs to fire for normal transitions. This severity should be a 1 if this was the only local effect. The fault current case in row 7 is much more severe, however, and should be a 5 (I have made both H6 and 7 five accordingly -- should the local effect or the failure mode determine the severity?). PS19 QPI: Updated the effects as per above comment | [7 empty] | -1305
SV104-1306 |  |  |  | Power not available from one of the input connectors. | Input power redundancy lost to one SCR gate driver board. If second power is affected the SCR gate driver board will not be functional. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 3 | Vibration. Improper bend radius during assembly. PSB connectivity failure from SCR. | Connectors with secure contact mating. | 2 | 6 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | None. | 5 | 30 | None. | None. | If the SCR gate measurement circuits detect this, injection mode shall not be allowed as the IGBTs will be unprotected from fault currents in the affected direction. | AI: This is high severity. If the SCR gate measurement circuits detect this, we should not go into injection mode as the IGBTs will be unprotected from fault currents in the affected direction. I have edited column G (see underlined text), and recommend we check with the h/w and f/w teams during the global call if they agree with my edits. PS19 QPI: Updated the effects as per above comment | [7 empty] | -1306
SV104-1307 | Input Reverse Polarity Protection Diode. | D114, D146 | To provide protection against reverse polarity inputs. | Diodes on both rails fail-open. | No power to the affected SCR gate driver board. Fault-current handling not available in one direction. Device will be unable to initiate the trigger for all SCRs in one direction when moving from injection mode to monitoring mode and vice versa. | During mode transition, no SCR will be handling the line current in one direction. IGBTs may get damaged in case of surge current event, if loss of SCRs occurs in injection mode. Device's default behavior will be to disallow injection mode operation. The device is capable of injection, however, and end user may request to override this protection. | Affected device and its associated group of devices will transit to monitoring mode. System will keep working with reduced injection capability. | 4 | Over Current. De-gradation of components. | Usage of over-rated components. | 2 | 8 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | On board SCR gate current measurement. | 1 | 8 | In Bypass Telemetry field 'SCR and Clamp Board Status' will show following: Cable break detected | On SmartInterface following Alarm will be raised: SCR Driver Board Malfunctioning | If the SCR gate measurement circuits detect this, injection mode shall not be allowed as the IGBTs will be unprotected from fault currents in the affected direction. | SJ: No Comment AI: same comments as R6 & R7 PS19 QPI: Updated the effects as per above comment | [7 empty] | -1307
SV104-5070 |  |  |  | Diodes on both rails fail-short.. | Protection against reverse polarity will not be available. In case a reverse polarity input is connected to the board, on-board electronics will be damaged. Overcurrent will cause the diode to eventually fail-open. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 3 | Over Current. De-gradation of components. | Usage of over-rated components. | 1 | 3 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | None. | 5 | 15 | None. | None. | If the SCR gate measurement circuits detect this, injection mode shall not be allowed as the IGBTs will be unprotected from fault currents in the affected direction. | AI: same comments as R6 & R7. Additionally, the VSLs will not get damaged in v1.04, but the IGBTs are vulnerable. I have adjusted F9 accordingly. | [7 empty] | -5070
SV104-1308 |  |  |  | Diode on one rail fails-open. | Loss of single 30 V rail. Redundant 30 V supply will provide power to on-board electronics | Device can operate in both injection and monitoring mode. | System will keep working normally. | 3 | Over Current. De-gradation of components. | Usage of over-rated components. | 1 | 3 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | None. | 5 | 15 | None. | None. | If the SCR gate measurement circuits detect this, injection mode shall not be allowed as the IGBTs will be unprotected from fault currents in the affected direction. | AI: No comment. | [7 empty] | -1308
SV104-5071 |  |  |  | Diode on one rail fails-short. | No immediate effect. Overcurrent will cause the diode to eventually fail-open. Loss of single 30 V rail. Redundant 30 V supply will provide power to on-board electronics | Device can operate in both injection and monitoring mode. | System will keep working normally. | 3 | Over Current. De-gradation of components. | Usage of over-rated components. | 1 | 3 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | None. | 5 | 15 | None. | None. | If the SCR gate measurement circuits detect this, injection mode shall not be allowed as the IGBTs will be unprotected from fault currents in the affected direction. | SJ: No Comment | [7 empty] | -5071
SV104-1309 | Positive 5 V Power Supply Circuit - Input Side Noise Filtration Inductor. | L8 | Switching supply harmonics suppression. | Inductor fails-open. | Loss of single 5 V supply. Redundant 5 V supply will provide power to on-board electronics | Device can operate in both injection and monitoring mode. | System will keep working normally. | 1 | Over Current. De-gradation of components. | Usage of over-rated components. | 1 | 1 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | None. | 5 | 5 | None. | None. |  | AI: No comment. | [7 empty] | -1309
SV104-5072 |  |  |  | Inductor fails-short. | Noise can affect performance of onboard surge detection circuit for positive half cycle. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 1 | Over Current. De-gradation of components. | Usage of over-rated components. | 1 | 1 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | None. | 5 | 5 | None. | None. |  | Reviewer: only filtration will be effected PS19 Q&PI: Updated | [7 empty] | -5072
SV104-1310 | Positive 5 V Power Supply Circuit - Input Side Bypass Capacitors. | C156, C157 | To filter out noise. To suppress input spikes. | Capacitor fails-open. | Noise can affect performance of onboard surge detection circuit for positive half cycle. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 1 | Over Current. De-gradation of components. | Usage of over-rated components. | 1 | 1 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | None. | 5 | 5 | None. | None. | [9 empty] | -1310
SV104-5073 |  |  |  | Capacitor fails-short. | Both 30 V rails will be shorted to ground. No power to the affected SCR gate driver board. Fault-current handling not available in one direction. Device will be unable to initiate the trigger for all SCRs in one direction when moving from injection mode to monitoring mode and vice versa. | During mode transition, no SCR will be handling the line current in one direction. IGBTs may get damaged in case of surge current event, if loss of SCRs occurs in injection mode. Device's default behavior will be to disallow injection mode operation. The device is capable of injection, however, and end user may request to override this protection. | Affected device and its associated group of devices will transit to monitoring mode. System will keep working with reduced injection capability. | 4 | Over Current. De-gradation of components. | Usage of over-rated components. | 1 | 4 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | On board SCR gate current measurement. | 1 | 4 | In Bypass Telemetry field 'SCR and Clamp Board Status' will show following: Cable break detected | On SmartInterface following Alarm will be raised: SCR Driver Board Malfunctioning | If the SCR gate measurement circuits detect this, injection mode shall not be allowed as the IGBTs will be unprotected from fault currents in the affected direction. | SJ: No Comment | [7 empty] | -5073
SV104-1311 | Positive 5 V Power Supply Circuit - 12 V Zener Diode. | D105 | Overvoltage protection for regulator IC. | Diode fails-open. | Overvoltage protection will be compromised, however higher voltages will be clamped internally with a 5.8 V Zener diode. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 2 | Over Voltage De-gradation of components. | Usage of over-rated components. | 2 | 4 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | None. | 5 | 20 | None. | None. | [9 empty] | -1311
SV104-5074 |  |  |  | Diode fails-short. | 5V supply not available to the affected SCR gate driver board. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 3 | Over Current. De-gradation of components. | Usage of over-rated components. | 1 | 3 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | None. | 5 | 15 | None. | None. | If the SCR gate measurement circuits detect this, injection mode shall not be allowed as the IGBTs will be unprotected from fault currents in the affected direction. | SJ: No Comment | [7 empty] | -5074
SV104-1312 | Positive 5 V Power Supply Circuit - Under Voltage Lockout Resistor Divider. | R180, R183, R474 | Adjust under voltage lockout for regulator IC. | One of the series resistor fails-open. | Enable pin of regulator IC will experience greater than Max(8.4V) voltages which will damage the regulator permanently. Redundant 5 V supply will provide power to onboard electronics | Device can operate in both injection and monitoring mode. | System will keep working normally. | 1 | Over Current. De-gradation of components. | Usage of over-rated components. | 1 | 1 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | None. | 5 | 5 | None. | None. | [9 empty] | -1312
SV104-5075 |  |  |  | High-side resistor fails-short. | Overcurrent will cause the resistor to eventually fail-open. Enable pin of regulator IC will experience greater than Max(8.4V) voltages which will damage the regulator permanently Redundant 5 V supply will provide power to onboard electronics | Device can operate in both injection and monitoring mode. | System will keep working normally. | 1 | Over Current. De-gradation of components. | Usage of over-rated components. | 1 | 1 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | None. | 5 | 5 | None. | None. | [9 empty] | -5075
SV104-5076 |  |  |  | Low-side resistor fails-short. | Less than 1.2 V at enable pin of regulator IC will disable the regulator. Redundant 5 V supply will provide power to onboard electronics | Device can operate in both injection and monitoring mode. | System will keep working normally. | 1 | Over Current. De-gradation of components. | Usage of over-rated components. | 1 | 1 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | None. | 5 | 5 | None. | None. | [9 empty] | -5076
SV104-1313 | Positive 5 V Power Supply Circuit - Timing Resistor. | R184 | To set switching frequency. | Resistor fails-open | Loss of single 5 V supply. Redundant 5 V supply will provide power to onboard electronics | Device can operate in both injection and monitoring mode. | System will keep working normally. | 1 | De-gradation of components. | Usage of over-rated components. | 1 | 1 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | None. | 5 | 5 | None. | None. | [9 empty] | -1313
SV104-5077 |  |  |  | Resistor fails-short. | Loss of single 5 V supply. Redundant 5 V supply will provide power to onboard electronics | Device can operate in both injection and monitoring mode. | System will keep working normally. | 1 | De-gradation of components. | Usage of over-rated components. | 1 | 1 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | None. | 5 | 5 | None. | None. | [9 empty] | -5077
SV104-1314 | Positive 5 V Power Supply Circuit - Bootstrap Capacitor. | C151 | To supply switching currents to the high and low side gate drivers. | Capacitor fails-open. | Loss of single 5 V supply. Redundant 5 V supply will provide power to onboard electronics | Device can operate in both injection and monitoring mode. | System will keep working normally. | 1 | Overvoltage. De-gradation of components. | Usage of over-rated components. | 1 | 1 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | None. | 5 | 5 | None. | None. | [9 empty] | -1314
SV104-5078 |  |  |  | Capacitor fails-short. | Loss of single 5 V supply. Redundant 5 V supply will provide power to onboard electronics | Device can operate in both injection and monitoring mode. | System will keep working normally. | 1 | Overvoltage. De-gradation of components. | Usage of over-rated components. | 1 | 1 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | None. | 5 | 5 | None. | None. | [9 empty] | -5078
SV104-1315 | Positive 5 V Power Supply Circuit - Catch Diode. | D76 | Maintain voltage at output. | Diode fails-open. | Voltage maintenance at regulator's output will be affected if heavily loaded. The overall circuit might get damaged permanently due to voltage spikes | Device can operate in both injection and monitoring mode. | System will keep working normally. | 1 | Overvoltage. De-gradation of components. | Usage of over-rated components. | 2 | 2 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | None. | 5 | 10 | None. | None. | [9 empty] | -1315
SV104-5079 |  |  |  | Diode fails-short. | Internal MOSFET's source will be shorted to ground. Loss of single 5 V supply. Redundant 5 V supply will provide power to onboard electronics | Device can operate in both injection and monitoring mode. | System will keep working normally. | 1 | Overvoltage. De-gradation of components. | Usage of over-rated components. | 1 | 1 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | None. | 5 | 5 | None. | None. | [9 empty] | -5079
SV104-1316 | Positive 5 V Power Supply Circuit - Output Inductor. | L7 | To maintain current flow during off state of the supply. | Inductor fails-open. | Loss of single 5 V supply. Redundant 5 V supply will provide power to onboard electronics | Device can operate in both injection and monitoring mode. | System will keep working normally. | 1 | Overvoltage. De-gradation of components. | Usage of over-rated components. | 1 | 1 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | None. | 5 | 5 | None. | None. | [9 empty] | -1316
SV104-5080 |  |  |  | Inductor fails-short. | Unstable operating of the switch mode power supply will happen. Loss of single 5 V supply. On-board electronics might get damaged due to unstable operation. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 1 | Overvoltage. De-gradation of components. | Usage of over-rated components. | 1 | 1 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | None. | 5 | 5 | None. | None. | [9 empty] | -5080
SV104-1317 | Positive 5 V Power Supply Circuit - Output Capacitor. | C152, C153, C154, C155, C368 | Filter inductor ripple currents Supply the increased load current until the regulator responds to the load step. | One of the output capacitors fail-open. | Reduced filtering capacity against output inductor's ripple currents. Capability to provide increased load current may be affected until the regulator responds to load step. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 1 | Overvoltage. De-gradation of components. | Usage of over-rated components. | 1 | 1 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | None. | 5 | 5 | None. | None. | [9 empty] | -1317
SV104-1318 |  |  |  | Multiple output capacitors fail-open. | No filtration available for noise. Noise can affect performance of onboard surge detection circuit for positive half cycle. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 1 | Over Current. De-gradation of components. | Usage of over-rated components. | 1 | 1 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | None. | 5 | 5 | None. | None. | [9 empty] | -1318
SV104-1319 | Positive 5 V Power Supply Circuit - Output Feedback Resistors. | R179, R182 | Provide output voltage feedback to the switcher to maintain output voltage accuracy. | High-side resistor fails-open. | Input voltage will be replicated at regulator output. Over Voltage at the output may damage the ideal diodes of both 5V and redundant supply and on board electronics may get damaged. Loss of both 5 V power supplies SCR driver board will not be functional. Fault-current handling will not be available in one direction. | During mode transition, no SCR will be handling the line current in one direction. IGBTs may get damaged in case of surge current event, if loss of SCRs occurs in injection mode. Device's default behavior will be to disallow injection mode operation. The device is capable of injection, however, and end user may request to override this protection. | System will keep working normally. | 3 | Over Current. De-gradation of components. | Usage of over-rated components. | 1 | 3 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | On board SCR gate current measurement. | 1 | 3 | In Bypass Telemetry field 'SCR and Clamp Board Status' will show following: Cable break detected | On SmartInterface following Alarm will be raised: SCR Driver Board Malfunctioning | If the SCR gate measurement circuits detect this, injection mode shall not be allowed as the IGBTs will be unprotected from fault currents in the affected direction. | Reviewer: Over Voltage at the output may damage the ideal diodes of both 5V and redundant supply and on board electronics may get damaged PS19 Q&PI: Updated Second review: This failure causes the loss of both 5 V power supplies, so the whole SCR driver board will not be functional so Fault-current handling not available in one direction. Device will be unable to initiate the trigger for all SCRs in one direction when moving from injection mode to monitoring mode and vice-versa. PLEASE UPDATE THE HIGHER LEVEL EFFECT COLUMN AND OTHER COLUMNS ACCORDINGLY PS19 Q&PI: Updated | [7 empty] | -1319
SV104-5081 |  |  |  | High-side resistor fails-short.. | Loss of single 5 V supply. Redundant 5 V supply will provide power to onboard electronics | Device can operate in both injection and monitoring mode. | System will keep working normally. | 1 | Overvoltage. De-gradation of components. | Usage of over-rated components. | 1 | 1 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | None. | 5 | 5 | None. | None. | [9 empty] | -5081
SV104-5082 |  |  |  | Low-side resistor fails-short. | Input voltage will be replicated at regulator output. Over Voltage at the output may damage the ideal diodes of both 5V and redundant supply and on board electronics may get damaged. Loss of both 5 V power supplies SCR driver board will not be functional. Fault-current handling will not be available in one direction. | During mode transition, no SCR will be handling the line current in one direction. IGBTs may get damaged in case of surge current event, if loss of SCRs occurs in injection mode. Device's default behavior will be to disallow injection mode operation. The device is capable of injection, however, and end user may request to override this protection. | System will keep working normally. | 3 | Over Current. De-gradation of components. | Usage of over-rated components. | 1 | 3 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | On board SCR gate current measurement. | 1 | 3 | In Bypass Telemetry field 'SCR and Clamp Board Status' will show following: Cable break detected | On SmartInterface following Alarm will be raised: SCR Driver Board Malfunctioning | If the SCR gate measurement circuits detect this, injection mode shall not be allowed as the IGBTs will be unprotected from fault currents in the affected direction. | Reviewer: Over Voltage at the output may damage the ideal diodes of both 5V and redundant supply and on board electronics may get damaged PS19 Q&PI: Updated Second review: This failure causes the loss of both 5 V power supplies, so the whole SCR driver board will not be functional so Fault-current handling not available in one direction. Device will be unable to initiate the trigger for all SCRs in one direction when moving from injection mode to monitoring mode and vice-versa. PLEASE UPDATE THE HIGHER LEVEL EFFECT COLUMN AND OTHER COLUMNS ACCORDINGLY PS19 Q&PI: Updated | [7 empty] | -5082
SV104-5083 |  |  |  | Low-side resistor fails-open. | Loss of single 5 V supply. Redundant 5 V supply will provide power to onboard electronics | Device can operate in both injection and monitoring mode. | System will keep working normally. | 1 | Overvoltage. De-gradation of components. | Usage of over-rated components. | 1 | 1 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | None. | 5 | 5 | None. | None. | [9 empty] | -5083
SV104-1320 | Positive 5 V Power Supply Circuit - Frequency Compensation Components At Error Amplifier Output. | C158, C159, R181 | To control the overall response of the IC's control system. | Capacitor (C158) fails-open. | IC response will cause supply to be affected. Performance of onboard surge detection circuit for positive half cycle. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 1 | Over Current. De-gradation of components. | Usage of over-rated components. | 1 | 1 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | None. | 5 | 5 | None. | None. |  | 1. power supply will be lost if c158 is shorted 2. performance will be effected if C159 is short. PS19: Q&PI: Updated | [7 empty] | -1320
SV104-9784 |  |  |  | Capacitor (C158) fails-short. | Loss of single 5 V supply. Redundant 5 V supply will provide power to onboard electronics | Device can operate in both injection and monitoring mode. | System will keep working normally. | 1 | Over Current. De-gradation of components. | Usage of over-rated components. | 1 | 1 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | None. | 5 | 5 | None. | None. | [9 empty] | -9784
SV104-9785 |  |  |  | Capacitor (C159) fails-open. | Loss of single 5 V supply. Redundant 5 V supply will provide power to onboard electronics | Device can operate in both injection and monitoring mode. | System will keep working normally. | 1 | Over Current. De-gradation of components. | Usage of over-rated components. | 1 | 1 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | None. | 5 | 5 | None. | None. | [9 empty] | -9785
SV104-5084 |  |  |  | Capacitor (C159) fails-short.. | Overcurrent will cause the capacitor to eventually fail-open. No filtration available for noise. Performance will be effected. Noise can affect performance of onboard surge detection circuit for positive half cycle. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 1 | Over Current. De-gradation of components. | Usage of over-rated components. | 1 | 1 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | None. | 5 | 5 | None. | None. | [9 empty] | -5084
SV104-1321 |  |  |  | Resistor fails-open. | Loss of single 5 V supply. Redundant 5 V supply will provide power to onboard electronics | Device can operate in both injection and monitoring mode. | System will keep working normally. | 1 | Over Current. De-gradation of components. | Usage of over-rated components. | 1 | 1 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | None. | 5 | 5 | None. | None. | [9 empty] | -1321
SV104-5085 |  |  |  | Resistor fails-short. | Overcurrent will cause the resistor to eventually fail-open. No filtration available for noise. Noise can affect performance of onboard surge detection circuit for positive half cycle. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 1 | Over Current. De-gradation of components. | Usage of over-rated components. | 1 | 1 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | None. | 5 | 5 | None. | None. | [9 empty] | -5085
SV104-1322 | Positive 5 V Power Supply Circuit - Ideal Diode. | U147 | Reverse Current Protection. | IC failure. (Permanent low). | Loss of single 5 V supply. Redundant 5 V supply will provide power to onboard electronics | Device can operate in both injection and monitoring mode. | System will keep working normally. | 3 | Over Current. De-gradation of components. | Usage of over-rated components. | 2 | 6 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | None. | 5 | 30 | None. | None. | [9 empty] | -1322
SV104-1323 | Positive 5 V Power Supply Circuit - Ideal Diode Output Inductor. | L16 | To suppress noise. | Inductor fails-open. | Loss of positive power supply for amplifiers used in surge detection circuit. Onboard line current sensing in one cycle will be affected. Reduced redundancy in case of fault events. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 3 | Over Current. De-gradation of components. | Usage of over-rated components. | 1 | 3 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | None. | 5 | 15 | None. | None. | [9 empty] | -1323
SV104-5086 |  |  |  | Inductor fails-short. | No immediate effect. High frequency ripple filtration will be effected. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 2 | Over Current. De-gradation of components. | Usage of over-rated components. | 1 | 2 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | None. | 5 | 10 | None. | None. |  | inductor is already short for low frequencies or DC, so there will be no any over current. If inductor looses its inductance due to a shortage, only high frequency ripple filtration will be effected, so very minor effect on surge detection circuit function PS19 Q&PI: Updated | [7 empty] | -5086
SV104-13649 | Positive 5 V Power Supply Circuit - Buck Regulator IC | U50 | Step down 30V to 5V. | IC failure. | Loss of single 5 V supply. Redundant 5 V supply will provide power to onboard electronics | Device can operate in both injection and monitoring mode. | System will keep working normally. | 3 | Over Current. De-gradation of components. | Usage of over-rated components. | 2 | 6 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | None. | 5 | 30 | None. | None. | [9 empty] | 13649
SV104-1324 | Negative 5 V Power Supply Circuit - Input Capacitor. | C303 | Filter out noise. Suppress input spikes. | Capacitor fails-open. | Noise filtration will be affected. Board performance might be affected. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 1 | Over Current. De-gradation of components. | Usage of over-rated components. | 1 | 1 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | None. | 5 | 5 | None. | None. | [9 empty] | -1324
SV104-5087 |  |  |  | Capacitor fails-short. | 30V supply directly shorted to ground. Loss of power to the board. | During mode transition, no SCR will be handling the line current in one direction. IGBTs may get damaged in case of surge current event, if loss of SCRs occurs in injection mode. Device's default behavior will be to disallow injection mode operation. The device is capable of injection, however, and end user may request to override this protection. | Affected device and its associated group of devices will transit to monitoring mode. System will keep working with reduced injection capability. | 4 | Over Current. De-gradation of components. | Usage of over-rated components. | 1 | 4 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | On board SCR gate current measurement. | 1 | 4 | In Bypass Telemetry field 'SCR and Clamp Board Status' will show following: Cable break detected | On SmartInterface following Alarm will be raised: SCR Driver Board Malfunctioning | [9 empty] | -5087
SV104-1325 | Negative 5 V Power Supply Circuit - Resistor Divider For Under Voltage Comparator Of Regulator IC. | R432, R434 | Maintain under voltage detection threshold. | High-side resistor fails-open. | Loss of negative 5 V supply. Onboard negative cycle line current sensing in one cycle will be affected. Surge detection will be affected. Worst case scenario, SCRD board will not be able to trigger SCR due to on-board detection. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 2 | Over Current. De-gradation of components. | Usage of over-rated components. | 1 | 2 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | None. | 5 | 10 | None. | None. | [9 empty] | -1325
SV104-5088 |  |  |  | High-side resistor fails-short. | 30V supply will directly appear across UVLO pin and will damage the IC. Worst case scenario Loss of negative 5 V supply. Onboard negative cycle line current sensing in one cycle will be affected. Surge detection will be affected. Worst case scenario, SCRD board will not be able to trigger SCR due to on-board detection. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 2 | Over Current. De-gradation of components. | Usage of over-rated components. | 1 | 2 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | None. | 5 | 10 | None. | None. | [9 empty] | -5088
SV104-5089 |  |  |  | Low-side resistor fails-open. | 30V supply will directly appear across UVLO pin and will damage the IC. Worst case scenario Loss of negative 5 V supply. Onboard negative cycle line current sensing in one cycle will be affected. Surge detection will be affected. Worst case scenario, SCRD board will not be able to trigger SCR due to on-board detection. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 2 | Over Current. De-gradation of components. | Usage of over-rated components. | 1 | 2 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | None. | 5 | 10 | None. | None. | [9 empty] | -5089
SV104-5090 |  |  |  | Low-side resistor fails-short. | Loss of negative 5 V supply. Onboard line current sensing in negative cycle will be affected. Surge detection will be affected. Worst case scenario, SCRD board will not be able to trigger SCR due to on-board detection. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 2 | Over Current. De-gradation of components. | Usage of over-rated components. | 1 | 2 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | None. | 5 | 10 | None. | None. | [9 empty] | -5090
SV104-1326 | Negative 5 V Power Supply Circuit - Bootstrap Capacitor. | C300 | Supply switching currents to the high and low side gate drivers. | Capacitor fails-open. | Loss of negative 5 V supply. Onboard line current sensing in negative cycle will be affected. Surge detection will be affected. Worst case scenario, SCRD board will not be able to trigger SCR due to on-board detection. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 2 | Over Current. De-gradation of components. | Usage of over-rated components. | 1 | 2 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | None. | 5 | 10 | None. | None. | [9 empty] | -1326
SV104-5091 |  |  |  | Capacitor fails-short. | Loss of negative 5 V supply. Onboard line current sensing in negative cycle will be affected. Surge detection will be affected. Worst case scenario, SCRD board will not be able to trigger SCR due to on-board detection. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 2 | Over Current. De-gradation of components. | Usage of over-rated components. | 1 | 2 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | None. | 5 | 10 | None. | None. | [9 empty] | -5091
SV104-1327 | Negative 5 V Power Supply Circuit - Decoupling Capacitor At Internal Vcc Regulator. | C305 | Filter out noise. Suppress input spikes. | Capacitor fails-open. | No immediate effect. Regulator may degrade over time. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 1 | Over Current. De-gradation of components. | Usage of over-rated components. | 2 | 2 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | None. | 5 | 10 | None. | None. | [9 empty] | -1327
SV104-5092 |  |  |  | Capacitor fails-short. | Loss of negative 5 V supply. Onboard line current sensing in negative cycle will be affected. Surge detection will be affected. Worst case scenario, SCRD board will not be able to trigger SCR due to on-board detection. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 2 | Over Current. De-gradation of components. | Usage of over-rated components. | 1 | 2 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | None. | 5 | 10 | None. | None. |  | Power supply will be lost because the internal regulator will no be supply any Vcc to internal devices PS19 Q&PI: Updated | [7 empty] | -5092
SV104-1328 | Negative 5 V Power Supply Circuit - Output Feedback Resistors. | R431, R435 | Maintain output voltage accuracy. | High-side resistor fails-open. | Negative over-voltage will happen and on-board electronics may get damaged Loss of negative 5 V supply. Onboard line current sensing in negative cycle will be affected. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 2 | Over Current. De-gradation of components. | Usage of over-rated components. | 1 | 2 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | None. | 5 | 10 | None. | None. |  | negative overvoltage will happen and on board electronics may get damaged PS19 Q&PI: Updated | [7 empty] | -1328
SV104-5093 |  |  |  | High-side resistor fails-short. | Loss of negative 5 V supply. Onboard line current sensing in negative cycle will be affected. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 2 | Over Current. De-gradation of components. | Usage of over-rated components. | 1 | 2 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | None. | 5 | 10 | None. | None. | [9 empty] | -5093
SV104-5094 |  |  |  | Low-side resistor fails-open. | Loss of negative 5 V supply. Onboard line current sensing in negative cycle will be affected. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 2 | Over Current. De-gradation of components. | Usage of over-rated components. | 1 | 2 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | None. | 5 | 10 | None. | None. |  | negative overvoltage will happen and on board electronics may get damaged PS19 Q&PI: Updated | [7 empty] | -5094
SV104-5095 |  |  |  | Low side resistor fails-short. | Loss of negative 5 V supply. Onboard line current sensing in negative cycle will be affected. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 2 | Over Current. De-gradation of components. | Usage of over-rated components. | 1 | 2 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | None. | 5 | 10 | None. | None. | [9 empty] | -5095
SV104-1329 | Negative 5 V Power Supply Circuit - On-Time Resistor. | R433 | Determine On-Time for the regulator. | Resistor fails-open. | Loss of negative 5 V supply. Onboard line current sensing in negative cycle will be affected. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 2 | Over Current. De-gradation of components. | Usage of over-rated components. | 1 | 2 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | None. | 5 | 10 | None. | None. | [9 empty] | -1329
SV104-5096 |  |  |  | Resistor fails-short. | Overcurrent will cause the resistor to eventually fail-open. Loss of negative 5 V supply. Onboard line current sensing in negative cycle will be affected. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 2 | Over Current. De-gradation of components. | Usage of over-rated components. | 1 | 2 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | None. | 5 | 10 | None. | None. | [9 empty] | -5096
SV104-1330 | Negative 5 V Power Supply Circuit - Decoupling Capacitor At On-Time Generator. | C306 | Filter out noise. Suppress input spikes. | Capacitor fails-open. | No immediate effect. Regulator may degrade over time. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 1 | Over Current. De-gradation of components. | Usage of over-rated components. | 2 | 2 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | None. | 5 | 10 | None. | None. | [9 empty] | -1330
SV104-5097 |  |  |  | Capacitor fails-short. | 30 V rail will be shorted to ground. On-board components will not be powered up till the time capacitor remains shorted. Overcurrent will cause the capacitor to eventually fail-open. | During mode transition, no SCR will be handling the line current in one direction. IGBTs may get damaged in case of surge current event, if loss of SCRs occurs in injection mode. Device's default behavior will be to disallow injection mode operation. The device is capable of injection, however, and end user may request to override this protection. | System will keep working normally. | 4 | Over Current. De-gradation of components. | Usage of over-rated components. | 1 | 4 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | On board SCR gate current measurement. | 1 | 4 | In Bypass Telemetry field 'SCR and Clamp Board Status' will show following: Cable break detected | On SmartInterface following Alarm will be raised: SCR Driver Board Malfunctioning | If the SCR gate measurement circuits detect this, injection mode shall not be allowed as the IGBTs will be unprotected from fault currents in the affected direction. | [8 empty] | -5097
SV104-1331 | Negative 5 V Power Supply Circuit - Output Voltage Ripple Filter. | R430, C302 | Filter out noise. Suppress ripples at output voltage. | Capacitor fails-open. | Ripple filtration will be effected. Onboard line current sensing in one cycle will be affected. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 1 | Over Current. De-gradation of components. | Usage of over-rated components. | 1 | 1 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | None. | 5 | 5 | None. | None. |  | if C302 or C301 is open, ripple filtration will be affected. Onboard line current sensing will be effected to a small extent PS19 Q&PI: Updated | [7 empty] | -1331
SV104-5098 |  |  |  | Capacitor fails-short. | Loss of negative 5 V supply. Onboard line current sensing in negative cycle will be affected. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 2 | Over Current. De-gradation of components. | Usage of over-rated components. | 1 | 2 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | None. | 5 | 10 | None. | None. | [9 empty] | -5098
SV104-1332 |  |  |  | Resistor fails-open. | No immediate effect. Noise filtration will be effected. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 1 | Over Current. De-gradation of components. | Usage of over-rated components. | 1 | 1 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | None. | 5 | 5 | None. | None. |  | only ripple filtration will be affected a little bit. Negligible effect on performance of current sensing circuit. PS19 Q&PI: Updated | [7 empty] | -1332
SV104-5099 |  |  |  | Resistor fails-short. | No immediate effect. Noise filtration will be effected. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 1 | Over Current. De-gradation of components. | Usage of over-rated components. | 1 | 1 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | None. | 5 | 5 | None. | None. |  | Ripple filtration and onboard line current sensing will be effected PS19 Q&PI: Updated | [7 empty] | -5099
SV104-1333 | Negative 5 V Power Supply Circuit - Output Transformer. | L18 | To provide isolation. | Winding fails-open. | Loss of negative 5 V supply. Onboard line current sensing in negative cycle will be affected. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 2 | Over Current. De-gradation of components. | Usage of over-rated components. | 1 | 2 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | None. | 5 | 10 | None. | None. | [9 empty] | -1333
SV104-5100 |  |  |  | Winding fails-short. . | Loss of negative 5 V supply. Onboard line current sensing in negative cycle will be affected. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 2 | Over Current. De-gradation of components. | Usage of over-rated components. | 1 | 2 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | None. | 5 | 10 | None. | None. | [9 empty] | -5100
SV104-1334 | Negative 5 V Power Supply Circuit - Output Diode. | D97 | Suppress AC spikes. | Diode fails-open. | Loss of negative 5 V supply. Onboard line current sensing in negative cycle will be affected. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 2 | Over Current. De-gradation of components. | Usage of over-rated components. | 2 | 4 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | None. | 5 | 20 | None. | None. | [9 empty] | -1334
SV104-5101 |  |  |  | Diode fails-short. | No immediate effect. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 2 | Over Current. De-gradation of components. | Usage of over-rated components. | 1 | 2 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | None. | 5 | 10 | None. | None. | [9 empty] | -5101
SV104-13650 | Negative 5 V Power Supply Circuit - Buck Regulator | U132 | Step down 30V to 5V. | IC failure. | Loss of single negative 5 V supply. Onboard electronics using negative 5V supply will loose functioning voltages Surge detection will be affected. Worst case scenario, SCRD board will not be able to trigger SCR due to on-board detection. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 2 | Over Current. De-gradation of components. | Usage of over-rated components. | 2 | 4 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | None. | 5 | 20 | None. | None. | [9 empty] | 13650
SV104-13651 | Negative 5 V Power Supply Circuit - Common Mode Choke Capacitors | C299, C346 | To filter out ripples due to inductor. | Capacitor fails open. | No immediate effect. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 1 | Over Current. De-gradation of components. | Usage of over-rated components. | 2 | 2 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | None. | 5 | 10 | None. | None. | [9 empty] | 13651
SV104-13652 |  |  |  | Capacitor fails short. | Negative 5V supply will be shorted to ground. On-board components will not be powered up till the time capacitor remains shorted. Surge detection will be affected. Worst case scenario, SCRD board will not be able to trigger SCR due to on-board detection. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 2 | Over Current. De-gradation of components. | Usage of over-rated components. | 1 | 2 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | None. | 5 | 10 | None. | None. | [9 empty] | 13652
SV104-1335 | Negative 5 V Power Supply Circuit - Common Mode Choke. | L17 | To filter noise. | Winding fails-open. | Loss of negative 5 V supply. Onboard line current sensing in one cycle will be affected. Reduced redundancy in case of fault events | Device can operate in both injection and monitoring mode. | System will keep working normally. | 2 | Overvoltage. De-gradation of components. | Usage of over-rated components. | 1 | 2 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | None. | 5 | 10 | None. | None. | [9 empty] | -1335
SV104-5102 |  |  |  | Winding fails-short. . | Loss of negative 5 V supply. Onboard line current sensing in one cycle will be affected. Reduced redundancy in case of fault events | Device can operate in both injection and monitoring mode. | System will keep working normally. | 2 | Overvoltage. De-gradation of components. | Usage of over-rated components. | 1 | 2 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | None. | 5 | 10 | None. | None. | [9 empty] | -5102
| SCR Gate Driver Board - SVMC board Interface | [26 empty] | 0
SV104-1337 | Multi-Channel Buffers. | U93, U73 | Trigger SCRs with proper gate-to-cathode current pulse and continuous back porch current. | Multi-channel buffers failure. (Two SCR(s) are not triggered). | Gate current not available for 2 SCR channels in worst case. Loss of SCRs may cause remaining SCRs to overheat during fault. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 3 | Bad component batch. De-gradation of components. | Redundant VSLs are available to handle the fault current in monitoring mode. | 2 | 6 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | On board SCR gate current measurement. | 3 | 18 | "In Bypass Telemetry field 'SCR and Clamp Board Status' will show following: SCR 1 (Output Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 2 (Mid 1 Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 3 (Mid 2 Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 4 (Input Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) | None. | Alert to be generated for the user to communicate the unavailability of portion of SCR channels. [Firmware team] Implement logic in firmware design to close the VSLs in presence of this event. | [6 empty] | 0 | Approved | -1337
SV104-1338 |  |  |  | Multi-channel buffers failure Two SCR(s) are continuously triggered). | SCR gate current triggered continuously for 2 SCR channels in worst case. Device cannot enter into injection mode. At line current above 9-15 kA Pk, the affected SCRs will start conducting. | If device was in injection mode it will switch to monitoring mode. Device will remain in Monitoring mode as long as this issue persists. | Affected device and its associated group of devices will transit to monitoring mode. System will keep working with reduced injection capability. | 4 | Bad component batch. De-gradation of components. | Usage of over-rated components. | 2 | 8 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | SCR current measurement from Rogowski coil. | 2 | 16 | In Bypass Telemetry field 'SCR and Clamp Board Status' will show following: SCR 1 (Output Side): Two SCRs Fired OR SCR 2 (Mid 1 Side): Two SCRs Fired OR SCR 3 (Mid 2 Side): Two SCRs Fired OR SCR 4 (Input Side): Two SCRs Fired | On SmartInterface following Alarm will be raised: If SCR > 100 SCR Failed Short If Line Current > 80A && SCR firing duration = 10 mins SCR Prolong Firing | Alert to be generated for the user to communicate the continuous triggering of portion of SCR channels. [Firmware team] 1) Implement logic in firmware design to close the VSLs in presence of this event. 2) Keep monitoring system temperature and line current. In case of sharply rising system temperature, generate an alert to ask for engaging of external bypass. | [6 empty] | 0 | Approved | -1338
SV104-1339 | SVMC board Interface - Optical Cable. | U48, U75 | Interface SVMC board with SCR driver board. | One 'Enable' optical signals between SVMC board and SCR driver board becomes disconnected. | SVMC board will lose control of 2 SCRs in worst case. SVMC board will be unable to initiate the trigger for 2 SCRs when moving from injection mode to monitoring mode and vice-versa. In case of a surge current event, all SCRs will be triggered through on board sensor. | During mode transition, only 2 SCRs will be handling the line current in one direction. | System will keep working normally. | 3 | Vibration. Improper bend radius during assembly. | Connectors with secure contact mating. In case of a surge current event, all SCRs will be triggered through on board sensor. | 2 | 6 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | On board SCR gate current measurement. | 3 | 18 | "In Bypass Telemetry field 'SCR and Clamp Board Status' will show following: SCR 1 (Output Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 2 (Mid 1 Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 3 (Mid 2 Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 4 (Input Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) | None. | Alert to be generated for the user to communicate the failure of one portion of SCR triggering path. | [6 empty] | 0 | Approved | -1339
SV104-1340 |  |  | Interface SVMC board with SCR driver board. | Both 'Enable' optical signals between SVMC board and SCR driver board become disconnected. | SVMC board will lose control of all SCRs in one direction in worst case. SVMC board will be unable to initiate the trigger for all SCRs when moving from injection mode to monitoring mode and vice versa. In case of a surge current event, all SCRs will be triggered through on board sensor. | Device can operate in both monitoring and injection mode. During VSL closing time of 80 msec, current for 5 half cycles will flow through inverter. | System will keep working normally. | 4 | Vibration. Improper bend radius during assembly. | Connectors with secure contact mating. In case of a surge current event, all SCRs will be triggered through on board sensor. | 2 | 8 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | SCR current measurement from Rogowski coil. | 1 | 8 | In Bypass Telemetry field 'SCR Current' will show SCR < 40A | On SmartInterface following Alarm will be raised: Permanent Injection Lockout | Alert to be generated for the user to communicate the failure of one portion of SCR triggering path. | [6 empty] | 0 | Approved | -1340
SV104-1341 | Optical Receiver - Application Circuit - Inductor. | L6, L14 | Suppress supply voltage noise. | Inductor fails-open. | SVMC board will lose control of 2 SCRs in worst case. SVMC board will be unable to initiate the trigger for 3 SCRs when moving from injection mode to monitoring mode and vice versa. In case of a surge current event, all SCRs will be triggered through on board sensor. | During mode transition, only 2 SCRs will be handling the line current in one direction. | System will keep working normally. | 3 | Over Current. De-gradation of components. | Connectors with secure contact mating. In case of a surge current event, all SCRs will be triggered through on board sensor. | 1 | 3 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | On board SCR gate current measurement. | 3 | 9 | "In Bypass Telemetry field 'SCR and Clamp Board Status' will show following: SCR 1 (Output Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 2 (Mid 1 Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 3 (Mid 2 Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 4 (Input Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) | None. | Alert to be generated for the user to communicate the failure of one portion of SCR triggering path. | [6 empty] | 0 |  | -1341
SV104-5013 |  |  |  | Loss of inductance. | Reduced filtration against noise and transients. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 2 | Over Current. De-gradation of components. | Usage of over-rated components. | 1 | 2 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | None. | 5 | 10 | None. | None. | Alert to be generated for the user to communicate the failure of one portion of SCR triggering path. | inductor is already short. If it looses its inductance due to a shortage only ripple filtration will be effected. Device will function normally PS19: Updated. | [7 empty] | -5013
SV104-1342 | Optical Receiver - Application Circuit - Filtering Capacitors. | C147, C148, C149, C183, C184, C198 | Suppress supply voltage noise. | Capacitor fails-open. | Reduced filtration against noise and transients. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 1 | Bad capacitor batch. | Usage of over-rated components. | 2 | 2 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | None. | 5 | 10 | None. | None. | [Hardware team] 1. Properly space capacitors from board edge. 2. Review the design and consider the provision to isolate the shorted capacitor. [Process team] Qualified capacitor vendors. | [8 empty] | -1342
SV104-5104 |  |  |  | Capacitor fails-short. | SVMC board will lose control of 2 SCRs in worst case. SVMC board will be unable to initiate the trigger for 3 SCRs when moving from injection mode to monitoring mode and vice versa. In case of a surge current event, all SCRs will be triggered through on board sensor. | During mode transition, only 2 SCRs will be handling the line current in one direction. | System will keep working normally. | 3 | Over Current. De-gradation of components. | Connectors with secure contact mating. In case of a surge current event, all SCRs will be triggered through on board sensor. | 2 | 6 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | On board SCR gate current measurement. | 3 | 18 | "In Bypass Telemetry field 'SCR and Clamp Board Status' will show following: SCR 1 (Output Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 2 (Mid 1 Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 3 (Mid 2 Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 4 (Input Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) | None. | Alert to be generated for the user to communicate the failure of one portion of SCR triggering path. | [8 empty] | -5104
SV104-13653 | Voltage Supply Filtering Capacitor | C182, C212, C288, C289, C293, C294, C295 | To filter supply voltage noise. | Capacitor fails-open. | No immediate effect. Noise at output may cause on-board electronics to malfunction. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 1 | Over Voltage De-gradation of components. | Usage of over-rated components. | 1 | 1 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | None. | 5 | 5 | None. | None. | [9 empty] | 13653
SV104-13654 |  |  |  | Capacitor fails-short. | No immediate effect. The respective active device will get stuck at low or high output. Cascading shortage of supply voltage capacitors may cause reduction of single SCR gate current. 5V supply loss. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 1 | Over Voltage De-gradation of components. | Usage of over-rated components. | 1 | 1 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | None. | 5 | 5 | None. | None. | [9 empty] | 13654
SV104-13655 | Input Resistor Single Inverter Gate IC | R467 | To limit current and avoid ringing. | Resistor fails open. | Surge Signal will not be available SCRD board. In case of a Surge event SCRs will be triggered through on board sensor. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 1 | Over Voltage De-gradation of components. | Usage of over-rated components. | 1 | 1 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | None. | 5 | 5 | None. | None. | [9 empty] | 13655
SV104-13656 |  |  |  | Resistor fails short. | No immediate effect. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 1 | Over Voltage De-gradation of components. | Usage of over-rated components. | 1 | 1 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | None. | 5 | 5 | None. | None. | [9 empty] | 13656
SV104-13657 | Non-Inverting Buffer - Pull-down Resistor | R175, R233 | To provide input to non-inverting buffer channels. | Resistor fails open. | No immediate effect. Worst case scenario, SCR Enable signal may not be available. In case of a Surge event SCRs will be triggered through on board sensor. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 1 | Over Voltage De-gradation of components. | Usage of over-rated components. | 1 | 1 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | None. | 5 | 5 | None. | None. | [9 empty] | 13657
SV104-13658 |  |  |  | Resistor fails short. | Input Signal is shorted to ground and SCR Enable signal will not be available. In case of a Surge event SCRs will be triggered through on board sensor. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 3 | Over Voltage De-gradation of components. | Usage of over-rated components. | 1 | 3 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | On board SCR gate current measurement. | 3 | 9 | "In Bypass Telemetry field 'SCR and Clamp Board Status' will show following: SCR 1 (Output Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 2 (Mid 1 Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 3 (Mid 2 Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 4 (Input Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) | None. | [9 empty] | 13658
SV104-13659 | Non-Inverting Buffer - Grounding Bit Resistor | R489, R490 | To provide grounding bits to non-inverting buffer channels. | Resistor fails open. | No immediate effect. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 1 | Over Voltage De-gradation of components. | Usage of over-rated components. | 1 | 1 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | None. | 5 | 5 | None. | None. | [9 empty] | 13659
SV104-13660 |  |  |  | Resistor fails short. | No immediate effect. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 1 | Over Voltage De-gradation of components. | Usage of over-rated components. | 1 | 1 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | None. | 5 | 5 | None. | None. | [9 empty] | 13660
SV104-1343 | Single Inverter Gate IC. | U125, U128, U129 | To isolate the enable signal. | IC failure. Permanent low. | SCR gate current triggered continuously for 2 SCR channels in worst case. Device cannot enter into injection mode. At line current above 9-15 kA Pk, the affected SCRs will start conducting. | If device was in injection mode it will switch to monitoring mode. Device will remain in Monitoring mode as long as this issue persists. | Affected device and its associated group of devices will transit to monitoring mode. System will keep working with reduced injection capability. | 4 | Bad component batch. | Usage of over-rated components. | 2 | 8 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | SCR current measurement from Rogowski coil. | 2 | 16 | In Bypass Telemetry field 'SCR and Clamp Board Status' will show following: SCR 1 (Output Side): Two SCRs Fired OR SCR 2 (Mid 1 Side): Two SCRs Fired OR SCR 3 (Mid 2 Side): Two SCRs Fired OR SCR 4 (Input Side): Two SCRs Fired | On SmartInterface following Alarm will be raised: If SCR > 100 SCR Failed Short If Line Current > 80A && SCR firing duration = 10 mins SCR Prolong Firing | Alert to be generated for the user to communicate the continuous triggering of portion of SCR channels. [Firmware team] 1) Implement logic in firmware design to close the VSLs in presence of this event. 2) Keep monitoring system temperature and line current. In case of sharply rising system temperature, generate an alert to ask for engaging of external bypass. | [8 empty] | -1343
SV104-1344 |  |  |  | IC failure. Permanent high. | Gate current not available for 2 SCR channels in worst case. Loss of SCRs may cause remaining SCRs to overheat during fault. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 3 | Bad component batch. | Redundant VSLs are available to handle the fault current in monitoring mode. | 2 | 6 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | On board SCR gate current measurement. | 3 | 18 | "In Bypass Telemetry field 'SCR and Clamp Board Status' will show following: SCR 1 (Output Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 2 (Mid 1 Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 3 (Mid 2 Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 4 (Input Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) | None. | Alert to be generated for the user to communicate the unavailability of portion of SCR channels. [Firmware team] Implement logic in firmware design to close the VSLs in presence of this event. | [6 empty] | 0 |  | -1344
SV104-1345 | And Gate IC. | U127, U130 | To implement hardware logic of signals. | IC failure. Permanent low. | SCR gate current triggered continuously for 2 SCR channels in worst case. Device cannot enter into injection mode. At line current above 9-15 kA Pk, the affected SCRs will start conducting. | If device was in injection mode it will switch to monitoring mode. Device will remain in Monitoring mode as long as this issue persists. | Affected device and its associated group of devices will transit to monitoring mode. System will keep working with reduced injection capability. | 4 | Bad component batch. | Usage of over-rated components. | 2 | 8 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | SCR current measurement from Rogowski coil. | 2 | 16 | In Bypass Telemetry field 'SCR and Clamp Board Status' will show following: SCR 1 (Output Side): Two SCRs Fired OR SCR 2 (Mid 1 Side): Two SCRs Fired OR SCR 3 (Mid 2 Side): Two SCRs Fired OR SCR 4 (Input Side): Two SCRs Fired | On SmartInterface following Alarm will be raised: If SCR > 100 SCR Failed Short If Line Current > 80A && SCR firing duration = 10 mins SCR Prolong Firing | Alert to be generated for the user to communicate the continuous triggering of portion of SCR channels. [Firmware team] 1) Implement logic in firmware design to close the VSLs in presence of this event. 2) Keep monitoring system temperature and line current. In case of sharply rising system temperature, generate an alert to ask for engaging of external bypass. | [8 empty] | -1345
SV104-1346 |  |  | To implement hardware logic of signals | IC failure. Permanent high. | Gate current not available for 2 SCR channels in worst case. Loss of SCRs may cause remaining SCRs to overheat during fault. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 3 | Bad component batch. | Redundant VSLs are available to handle the fault current in monitoring mode. | 2 | 6 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | On board SCR gate current measurement. | 3 | 18 | "In Bypass Telemetry field 'SCR and Clamp Board Status' will show following: SCR 1 (Output Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 2 (Mid 1 Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 3 (Mid 2 Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 4 (Input Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) | None. | Alert to be generated for the user to communicate the unavailability of portion of SCR channels. [Firmware team] Implement logic in firmware design to close the VSLs in presence of this event. | [8 empty] | -1346
| SCR Gate Driver Board - Isolated Constant Current Circuit | [26 empty] | 0
SV104-1348 | G-K Connector. | CON1, CON2, CON3, CON4, CON5 | Connect SCR Gate driver board to SCR. | Disconnection from SCR g-k connector or from driver board connector. | Loss of gate current for a single SCR. Remaining SCRs may see a higher current during fault in one direction only. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 3 | Vibration. Improper assembly. | 4 parallel SCRs in either direction to ensure loss of a single SCR will not endanger VSLs and other SCRs. | 2 | 6 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | On board SCR gate current measurement. | 3 | 18 | "In Bypass Telemetry field 'SCR and Clamp Board Status' will show following: SCR 1 (Output Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 2 (Mid 1 Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 3 (Mid 2 Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 4 (Input Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) | None. | Alert to be generated for the user to communicate the failure of one portion of SCR triggering path. | [6 empty] | 0 | Approved | -1348
SV104-1349 | Input Side Common Mode Choke. | L9, L10, L11, L12, L13 | Noise Suppression. | CMC fails-open. | Loss of gate current for a single SCR. Remaining SCRs will see a higher current during fault and transition in one direction only. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 3 | Over Current. De-gradation of components. | 4 parallel SCRs in either direction to ensure loss of a single SCR will not endanger VSLs and other SCRs. | 1 | 3 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | On board SCR gate current measurement. | 3 | 9 | "In Bypass Telemetry field 'SCR and Clamp Board Status' will show following: SCR 1 (Output Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 2 (Mid 1 Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 3 (Mid 2 Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 4 (Input Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) | None. | Alert to be generated for the user to communicate the failure of one portion of SCR triggering path. | [8 empty] | -1349
SV104-1350 | Input Side Capacitor Bank. | C86, C87, C88, C89, C90, C91, C92, C93, C94, C95, C96, C97, C98, C99, C100, C101, C102, C103, C104, C106, C107, C108, C109, C110, C111, C112, C113, C114, C115, C116, C117, C118, C119, C120, C121, C122, C123, C124, C125, C126, C127, C128, C129, C130, C131, C132, C133, C134, C139, C140 | To provide high current pulse. | One of the capacitors fail-open. | No immediate effect. Multiple capacitor connected in parallel to provide adequate current. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 1 | Over Current. De-gradation of components. | Usage of over-rated components. | 1 | 1 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | None. | 5 | 5 | None. | None. | [9 empty] | -1350
SV104-5106 |  |  |  | One of the capacitors fail-short. . | Overcurrent will cause the capacitor to fail-open. 30 V rail will be shorted to ground for the shorted duration. Loss of gate current for a single SCR till he shorted duration. Remaining SCRs will see a higher current during fault and transition in one direction only. |  | System will keep working normally. | 3 | Over Current. De-gradation of components. | 4 parallel SCRs in either direction to ensure loss of a single SCR will not endanger VSLs and other SCRs. | 1 | 3 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | On board SCR gate current measurement. | 3 | 9 | "In Bypass Telemetry field 'SCR and Clamp Board Status' will show following: SCR 1 (Output Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 2 (Mid 1 Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 3 (Mid 2 Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 4 (Input Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) | None. | Alert to be generated for the user to communicate the failure of one portion of SCR triggering path. | [8 empty] | -5106
SV104-1351 |  |  |  | Multiple output capacitors fail-open. | Loss of gate current for a single SCR. Remaining SCRs will see a higher current during fault and transition in one direction only. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 3 | Over Current. De-gradation of components. | Usage of over-rated components. | 1 | 3 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | On board SCR gate current measurement. | 3 | 9 | "In Bypass Telemetry field 'SCR and Clamp Board Status' will show following: SCR 1 (Output Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 2 (Mid 1 Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 3 (Mid 2 Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 4 (Input Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) | None. | Alert to be generated for the user to communicate the failure of one portion of SCR triggering path. | [8 empty] | -1351
SV104-1352 | Initial High Current Pulse Driver Circuit - 12 V Zener Diode. | D5, D20, D35, D50, D65 | Overvoltage protection. | Diode fails-open. | No overvoltage protection for high power MOSFET gate. In case of overvoltage MOSFET gate may get damaged. Under normal working conditions there will be no immediate effect. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 2 | Over Current. De-gradation of components. | Usage of over-rated components. | 2 | 4 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | None. | 5 | 20 | None. | None. | [9 empty] | -1352
SV104-5107 |  |  |  | Diode fails-short. | Overcurrent will cause the diode to eventually fail-open. No overvoltage protection for high power MOSFET gate. In case of overvoltage MOSFET gate may get damaged. Under normal working conditions there will be no immediate effect. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 2 | Over Current. De-gradation of components. | Usage of over-rated components. | 2 | 4 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | None. | 5 | 20 | None. | None. | [9 empty] | -5107
SV104-1353 | Initial High Current Pulse Driver Circuit - General Purpose Diode. | D116, D117, D118, D119, D120 | Overvoltage protection. | Diode fails-open. | No overvoltage protection for high power MOSFET gate. In case of overvoltage MOSFET gate may get damaged. Under normal working conditions there will be no immediate effect. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 2 | Over Current. De-gradation of components. | Usage of over-rated components. | 2 | 4 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | None. | 5 | 20 | None. | None. | [9 empty] | -1353
SV104-5108 |  |  |  | Diode fails-short. | Loss of gate current for a single SCR. Remaining SCRs will see a higher current during fault and transition in one direction only. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 3 | Over Current. De-gradation of components. | Usage of over-rated components. | 2 | 6 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | On board SCR gate current measurement. | 3 | 18 | "In Bypass Telemetry field 'SCR and Clamp Board Status' will show following: SCR 1 (Output Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 2 (Mid 1 Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 3 (Mid 2 Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 4 (Input Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) | None. | Alert to be generated for the user to communicate the failure of one portion of SCR triggering path. | [8 empty] | -5108
SV104-13661 | Initial High Current Pulse Driver Circuit - Medium Power Low Saturation Transistor Collector Resistor | R2, R36, R70, R104, R138 | Limiting current. | Resistor fails-open. | BJT will not be able to operate. Initial pulse current will not be available to affected SCR gate but continuous back porch current will still be there. SCR may turn on due to continuous back porch. There is a probability that SCR may not turn on due to unavailability of initial pulse. Remaining SCRs will see a higher current during fault and transition in one direction only. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 3 | Over Current. De-gradation of components. | 4 parallel SCRs in either direction to ensure loss of a single SCR will not endanger VSLs and other SCRs. | 1 | 3 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | On board SCR gate current measurement. | 3 | 9 | "In Bypass Telemetry field 'SCR and Clamp Board Status' will show following: SCR 1 (Output Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 2 (Mid 1 Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 3 (Mid 2 Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 4 (Input Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) | None. | [9 empty] | 13661
SV104-13662 |  |  |  | Resistor fails-short. | BJT will not be able to operate in the desired operation region. Worst case scenario, high power MOSFET will not be able to turn on. Overcurrent will cause the resistor to fail open. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 2 | Over Current. De-gradation of components. | 4 parallel SCRs in either direction to ensure loss of a single SCR will not endanger VSLs and other SCRs. | 1 | 2 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | None. | 5 | 10 | None. | None. | [9 empty] | 13662
SV104-1354 | Initial High Current Pulse Driver Circuit - Pull-Up Resistor In Series With 12 V Zener. | R1, R35, R69, R103, R137 | Overvoltage protection. | Resistor fails-open. | No overvoltage protection for high power MOSFET gate. In case of overvoltage MOSFET gate may get damaged. Under normal working conditions there will be no immediate effect. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 2 | Over Current. De-gradation of components. | Usage of over-rated components. | 1 | 2 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | None. | 5 | 10 | None. | None. | [9 empty] | -1354
SV104-5109 |  |  |  | Resistor fails-short. | Overcurrent will cause the resistor to eventually fail-open. No overvoltage protection for high power MOSFET gate. In case of overvoltage MOSFET gate may get damaged. Under normal working conditions there will be no immediate effect. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 2 | Over Current. De-gradation of components. | Usage of over-rated components. | 1 | 2 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | None. | 5 | 10 | None. | None. | [9 empty] | -5109
SV104-1355 | Initial High Current Pulse Driver Circuit - Medium Power Low Saturation Transistor. | Q2, Q7, Q14, Q17, Q22 | Overvoltage protection. | Both transistors fail-short. | Initial pulse current will not be available to affected SCR gate but continuous back porch current will still be there. SCR may turn on due to continuous back porch. There is a probability that SCR may not turn on due to unavailability of initial pulse. Remaining SCRs will see a higher current during fault and transition in one direction only. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 3 | Over Current. De-gradation of components. | 4 parallel SCRs in either direction to ensure loss of a single SCR will not endanger VSLs and other SCRs. | 2 | 6 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | On board SCR gate current measurement. | 3 | 18 | "In Bypass Telemetry field 'SCR and Clamp Board Status' will show following: SCR 1 (Output Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 2 (Mid 1 Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 3 (Mid 2 Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 4 (Input Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) | None. | Alert to be generated for the user to communicate the failure of one portion of SCR triggering path. | [8 empty] | -1355
SV104-1356 |  |  |  | Transistor fails-open. | Overvoltage protection for high power MOSFET gate will be compromised. In case of extreme overvoltage MOSFET gate will be protected via parallel reverse biased diode. Under normal working conditions there will be no immediate effect. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 2 | Over Current. De-gradation of components. | 4 parallel SCRs in either direction to ensure loss of a single SCR will not endanger VSLs and other SCRs. | 2 | 4 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | None. | 5 | 20 | None. | None. | [9 empty] | -1356
SV104-1357 | Initial High Current Pulse Driver Circuit - Medium Power Low Saturation Transistor Base Resistor. | R5, R39, R73, R107, R141 | To provide enough base-emitter voltage to turn transistor on. | Resistor fails-open. | Overvoltage protection for high power MOSFET gate will be compromised. In case of extreme overvoltage MOSFET gate will be protected via parallel reverse biased diode. Under normal working conditions there will be no immediate effect. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 2 | Over Current. De-gradation of components. | 4 parallel SCRs in either direction to ensure loss of a single SCR will not endanger VSLs and other SCRs. | 1 | 2 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | None. | 5 | 10 | None. | None. | [9 empty] | -1357
SV104-1358 | Initial High Current Pulse Driver Circuit - TVS Diode. | D3, D18, D33, D48, D63 | Transient Protection. | TVS diode fails-open. | Protection from transients will be reduced. Transformer may get saturated in case severe transients occurs. One SCR cannot trigger past first cycle in worst case. Under normal working conditions there will be no immediate effect. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 3 | High voltage transients | 4 parallel SCRs in either direction to ensure loss of a single SCR will not endanger VSLs and other SCRs. | 2 | 6 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | On board SCR gate current measurement. | 3 | 18 | "In Bypass Telemetry field 'SCR and Clamp Board Status' will show following: SCR 1 (Output Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 2 (Mid 1 Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 3 (Mid 2 Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 4 (Input Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) | None. | [9 empty] | -1358
SV104-5110 |  |  |  | TVS diode fails-short. | Overcurrent will cause the diode to eventually fail-open. Protection from transients will be reduced. Transformer may get saturated in case severe transients occurs. One SCR cannot trigger past first cycle in worst case. Under normal working conditions there will be no immediate effect. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 3 | High voltage transients | 4 parallel SCRs in either direction to ensure loss of a single SCR will not endanger VSLs and other SCRs. | 2 | 6 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | On board SCR gate current measurement. | 3 | 18 | "In Bypass Telemetry field 'SCR and Clamp Board Status' will show following: SCR 1 (Output Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 2 (Mid 1 Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 3 (Mid 2 Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 4 (Input Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) | None. | [9 empty] | -5110
SV104-1359 | Initial High Current Pulse Driver Circuit - High Power MOSFET. | Q1, Q6, Q11, Q16, Q21 | Provide high current pulse. | MOSFET fails-open. | High current will pass through the parallel connected resistor which may overheat and fail-open. Initial pulse current will not be available to affected SCR gate in worst case but continuous back porch current will still be there. There is a probability that SCR may not turn on due to unavailability of initial pulse Remaining SCRs will see a higher current during fault and transition in one direction only. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 3 | Over Current. De-gradation of components. | 4 parallel SCRs in either direction to ensure loss of a single SCR will not endanger VSLs and other SCRs. | 2 | 6 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | On board SCR gate current measurement. | 3 | 18 | "In Bypass Telemetry field 'SCR and Clamp Board Status' will show following: SCR 1 (Output Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 2 (Mid 1 Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 3 (Mid 2 Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 4 (Input Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) | None. | Alert to be generated for the user to communicate the failure of one portion of SCR triggering path. | [8 empty] | -1359
SV104-1360 | Initial High Current Pulse Driver Circuit - Parallel Connected Current Divider Resistors. | R3, R6, R37, R40, R71, R74, R105, R108, R139, R142 |  | One of the resistor fail-open. | High current will pass through the parallel connected resistor which may overheat and fail-open. Initial pulse current will not be available to affected SCR gate in worst case but continuous back porch current will still be there. There is a probability that SCR may not turn on due to unavailability of initial pulse Remaining SCRs will see a higher current during fault and transition in one direction only. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 3 | Over Current. De-gradation of components. | 4 parallel SCRs in either direction to ensure loss of a single SCR will not endanger VSLs and other SCRs. | 1 | 3 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | On board SCR gate current measurement. | 3 | 9 | "In Bypass Telemetry field 'SCR and Clamp Board Status' will show following: SCR 1 (Output Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 2 (Mid 1 Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 3 (Mid 2 Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 4 (Input Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) | None. | Alert to be generated for the user to communicate the failure of one portion of SCR triggering path. | [8 empty] | -1360
SV104-1361 | Initial High Current Pulse Driver Circuit - Transformer. | T1, T4, T7, T10, T13 | Provide high current pulse. | Transformer winding failure. | Initial pulse current will not be available to affected SCR gate but continuous back porch current will still be there. SCR may turn on due to continuous back porch. There is a probability that SCR may not turn on due to unavailability of initial pulse. Remaining SCRs will see a higher current during fault and transition in one direction only. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 3 | Over Current. De-gradation of components. | 4 parallel SCRs in either direction to ensure loss of a single SCR will not endanger VSLs and other SCRs. | 2 | 6 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | On board SCR gate current measurement. | 3 | 18 | "In Bypass Telemetry field 'SCR and Clamp Board Status' will show following: SCR 1 (Output Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 2 (Mid 1 Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 3 (Mid 2 Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 4 (Input Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) | None. | Alert to be generated for the user to communicate the failure of one portion of SCR triggering path. | Make a general winding failure case instead of fail-open for the transformer PS19 Q&PI Updated | [7 empty] | -1361
SV104-1362 | Initial High Current Pulse Driver Circuit - Transformer - Secondary Side Rectifier Diode. | D1, D16, D31, D46, D61 | Suppress AC spikes. | Diode fails-open. | Initial pulse current will not be available to affected SCR gate but continuous back porch current will still be there. SCR may turn on due to continuous back porch. There is a probability that SCR may not turn on due to unavailability of initial pulse. Remaining SCRs will see a higher current during fault and transition in one direction only. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 3 | Over Current. De-gradation of components. | 4 parallel SCRs in either direction to ensure loss of a single SCR will not endanger VSLs and other SCRs. | 2 | 6 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | On board SCR gate current measurement. | 3 | 18 | "In Bypass Telemetry field 'SCR and Clamp Board Status' will show following: SCR 1 (Output Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 2 (Mid 1 Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 3 (Mid 2 Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 4 (Input Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) | None. | Alert to be generated for the user to communicate the failure of one portion of SCR triggering path. | [8 empty] | -1362
SV104-5111 |  |  |  | Diode fails-short. | Overcurrent will cause the diode to eventually fail-open. Initial pulse current will not be available to affected SCR gate but continuous back porch current will still be there. SCR may turn on due to continuous back porch. There is a probability that SCR may not turn on due to unavailability of initial pulse. Remaining SCRs will see a higher current during fault and transition in one direction only. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 3 | Over Current. De-gradation of components. | 4 parallel SCRs in either direction to ensure loss of a single SCR will not endanger VSLs and other SCRs. | 2 | 6 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | On board SCR gate current measurement. | 3 | 18 | "In Bypass Telemetry field 'SCR and Clamp Board Status' will show following: SCR 1 (Output Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 2 (Mid 1 Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 3 (Mid 2 Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 4 (Input Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) | None. | Alert to be generated for the user to communicate the failure of one portion of SCR triggering path. | [8 empty] | -5111
SV104-1363 | Initial High Current Pulse Driver Circuit - Non-Inverting Buffer. | U44, U52, U53, U54, U55 | To isolate the signal. | Output stuck at low. | Initial pulse current will not be available to affected SCR gate but continuous back porch current will still be there. SCR may turn on due to continuous back porch. There is a probability that SCR may not turn on due to unavailability of initial pulse. Remaining SCRs will see a higher current during fault and transition in one direction only. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 3 | Over Current. De-gradation of components. | 4 parallel SCRs in either direction to ensure loss of a single SCR will not endanger VSLs and other SCRs. | 2 | 6 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | On board SCR gate current measurement. | 3 | 18 | "In Bypass Telemetry field 'SCR and Clamp Board Status' will show following: SCR 1 (Output Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 2 (Mid 1 Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 3 (Mid 2 Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 4 (Input Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) | None. | Alert to be generated for the user to communicate the failure of one portion of SCR triggering path. | [8 empty] | -1363
SV104-1364 | Initial High Current Pulse Driver Circuit - Non-Inverting Buffer. |  | Isolate the input signal . | Output stuck at high. | Pulse current circuit fails-short after providing an initial pulse. SCR is not triggered. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 3 | Over Current. De-gradation of components. | 4 parallel SCRs in either direction to ensure loss of a single SCR will not endanger VSLs and other SCRs. | 2 | 6 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | On board SCR gate current measurement. | 3 | 18 | "In Bypass Telemetry field 'SCR and Clamp Board Status' will show following: SCR 1 (Output Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 2 (Mid 1 Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 3 (Mid 2 Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 4 (Input Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) | None. | Alert to be generated for the user to communicate the failure of one portion of SCR triggering path. | [8 empty] | -1364
SV104-13663 | Initial High Current Pulse Driver Circuit - Gate Driver Low Side | U2, U11, U20, U29, U38 | To drive Low Side MOSET for initial pulse current. | IC failure. | Initial pulse current will not be available to affected SCR gate but continuous back porch current will still be there. SCR may turn on due to continuous back porch. There is a probability that SCR may not turn on due to unavailability of initial pulse. Remaining SCRs will see a higher current during fault and transition in one direction only. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 3 | Over Current. De-gradation of components. | 4 parallel SCRs in either direction to ensure loss of a single SCR will not endanger VSLs and other SCRs. | 2 | 6 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | None. | 5 | 30 | None. | None. | [9 empty] | 13663
SV104-13664 | Initial High Current Pulse Driver Circuit - Pull-up Resistor | R11, R45, R79, R113, R147 | To provide input voltage for MOSFET Gate driver. | Resistor fails-open. | Initial pulse current will not be available to affected SCR gate but continuous back porch current will still be there. SCR may turn on due to continuous back porch. There is a probability that SCR may not turn on due to unavailability of initial pulse. Remaining SCRs will see a higher current during fault and transition in one direction only. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 3 | Over Current. De-gradation of components. | 4 parallel SCRs in either direction to ensure loss of a single SCR will not endanger VSLs and other SCRs. | 1 | 3 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | None. | 5 | 15 | None. | None. | [9 empty] | 13664
SV104-13665 |  |  |  | Resistor fails-short. | Overcurrent may cause damage to MOSFET. Worst case scenario, the MOSFET fails open. Initial pulse current will not be available to affected SCR gate but continuous back porch current will still be there. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 3 | Over Current. De-gradation of components. | 4 parallel SCRs in either direction to ensure loss of a single SCR will not endanger VSLs and other SCRs. | 1 | 3 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | None. | 5 | 15 | None. | None. | [9 empty] | 13665
SV104-13666 | Initial High Current Pulse Driver Circuit - Non-Inverting Buffer Input Resistor | R10, R44, R78, R112, R146 | To provide Pulse Enable input signal for initial high current pulse. | Resistor fails-open. | Initial pulse current will not be available to affected SCR gate but continuous back porch current will still be there. SCR may turn on due to continuous back porch. There is a probability that SCR may not turn on due to unavailability of initial pulse. Remaining SCRs will see a higher current during fault and transition in one direction only. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 2 | Over Current. De-gradation of components. | 4 parallel SCRs in either direction to ensure loss of a single SCR will not endanger VSLs and other SCRs. | 1 | 2 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | None. | 5 | 10 | None. | None. | [9 empty] | 13666
SV104-13667 |  |  |  | Resistor fails-short. | No immediate effect. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 1 | Over Current. De-gradation of components. | Usage of over-rated components. | 1 | 1 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | None. | 5 | 5 | None. | None. | [9 empty] | 13667
SV104-1365 | Initial High Current Pulse Driver Circuit - 60 V MOSFET. | Q26, Q27, Q28, Q29, Q30 | Provide enable signal to MOSFET driver IC. | MOSFET fails-open. | Initial pulse current will not be available to affected SCR gate but continuous back porch current will still be there. SCR may turn on due to continuous back porch. There is a probability that SCR may not turn on due to unavailability of initial pulse. Remaining SCRs will see a higher current during fault and transition in one direction only. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 3 | Over Current. De-gradation of components. | 4 parallel SCRs in either direction to ensure loss of a single SCR will not endanger VSLs and other SCRs. | 2 | 6 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | None. | 5 | 30 | None. | None. | Alert to be generated for the user to communicate the failure of one portion of SCR triggering path. | [8 empty] | -1365
SV104-1366 |  |  |  | MOSFET fails-short. | Pulse current circuit fails-short after providing an initial pulse. SCR is not triggered. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 3 | Over Current. De-gradation of components. | 4 parallel SCRs in either direction to ensure loss of a single SCR will not endanger VSLs and other SCRs. | 2 | 6 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | None. | 5 | 30 | None. | None. | Alert to be generated for the user to communicate the failure of one portion of SCR triggering path. | [8 empty] | -1366
SV104-1367 | Initial High Current Pulse Driver Circuit - MOSFET Driver Input Side Resistor. | R203, R204, R205, R206, R207 | Limit the current. | Resistor fails-open. | Initial pulse current will not be available to affected SCR gate but continuous back porch current will still be there. SCR may turn on due to continuous back porch. There is a probability that SCR may not turn on due to unavailability of initial pulse. Remaining SCRs will see a higher current during fault and transition in one direction only. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 3 | Over Current. De-gradation of components. | 4 parallel SCRs in either direction to ensure loss of a single SCR will not endanger VSLs and other SCRs. | 1 | 3 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | None. | 5 | 15 | None. | None. | Alert to be generated for the user to communicate the failure of one portion of SCR triggering path. | Initial pulse current will not be available to affected SCR gate but continuous back porch current will still be there. SCR may turn on due to continuous back porch. There is a probability that SCR may not turn on due to unavailability of initial pulse. Remaining SCRs will see a higher current during fault and transition in one direction only. 2. Add resistor fail short case in which gate ringing will effect the life of the MOSFET. PS19 Q&PI: Updated | [7 empty] | -1367
SV104-9786 |  |  |  | Resistor fails-short. | No immediate effect. Gate ringing will effect the life of the MOSFET. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 2 | Over Current. De-gradation of components. | 4 parallel SCRs in either direction to ensure loss of a single SCR will not endanger VSLs and other SCRs. | 1 | 2 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | None. | 5 | 10 | None. | None. | Alert to be generated for the user to communicate the failure of one portion of SCR triggering path. | Initial pulse current will not be available to affected SCR gate but continuous back porch current will still be there. SCR may turn on due to continuous back porch. There is a probability that SCR may not turn on due to unavailability of initial pulse. Remaining SCRs will see a higher current during fault and transition in one direction only. 2. Add resistor fail short case in which gate ringing will effect the life of the MOSFET. PS19 Q&PI: Updated | [7 empty] | -9786
SV104-1368 | Initial High Current Pulse Driver Circuit - MOSFET Driver Output Resistor. | R12, R46, R80, R114, R148 | Avoid ringing. | Resistor fails-open. | Initial pulse current will not be available to affected SCR gate but continuous back porch current will still be there. SCR may turn on due to continuous back porch. There is a probability that SCR may not turn on due to unavailability of initial pulse. Remaining SCRs will see a higher current during fault and transition in one direction only. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 3 | Over Current. De-gradation of components. | 4 parallel SCRs in either direction to ensure loss of a single SCR will not endanger VSLs and other SCRs. | 1 | 3 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | None. | 5 | 15 | None. | None. | Alert to be generated for the user to communicate the failure of one portion of SCR triggering path. | [8 empty] | -1368
SV104-1369 |  |  |  | Resistor fails-short. | No immediate effect. MOSFET will dissipate more power, ultimately its life is de-graded. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 1 | Over Current. De-gradation of components. | 4 parallel SCRs in either direction to ensure loss of a single SCR will not endanger VSLs and other SCRs. | 1 | 1 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | None. | 5 | 5 | None. | None. | Alert to be generated for the user to communicate the failure of one portion of SCR triggering path. | [8 empty] | -1369
SV104-1370 | Initial High Current Pulse Driver Circuit - Low Side MOSET. | Q3, Q8, Q13, Q18, Q23 | To enable initial pulse current. | MOSFET fails-short. | Pulse current circuit fails-short after providing an initial pulse. SCR is not triggered. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 3 | Over Current. De-gradation of components. | 4 parallel SCRs in either direction to ensure loss of a single SCR will not endanger VSLs and other SCRs. | 2 | 6 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. |  | 3 | 18 | "In Bypass Telemetry field 'SCR and Clamp Board Status' will show following: SCR 1 (Output Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 2 (Mid 1 Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 3 (Mid 2 Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 4 (Input Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) | None. | Alert to be generated for the user to communicate the failure of one portion of SCR triggering path. | [8 empty] | -1370
SV104-1371 |  |  |  | MOSFET fails-open. | Initial pulse current will not be available to affected SCR gate but continuous back porch current will still be there. SCR may turn on due to continuous back porch. There is a probability that SCR may not turn on due to unavailability of initial pulse. Remaining SCRs will see a higher current during fault and transition in one direction only. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 3 | Over Current. De-gradation of components. | 4 parallel SCRs in either direction to ensure loss of a single SCR will not endanger VSLs and other SCRs. | 2 | 6 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. |  | 3 | 18 | "In Bypass Telemetry field 'SCR and Clamp Board Status' will show following: SCR 1 (Output Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 2 (Mid 1 Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 3 (Mid 2 Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 4 (Input Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) | None. | Alert to be generated for the user to communicate the failure of one portion of SCR triggering path. | [8 empty] | -1371
SV104-1372 | Continuous Back Porch Current Driver Circuit - Transformers. | T2, T3, T5, T6, T8, T9, T11, T12, T14, T15 | Provide continuous back-porch current. | Single transformer winding failure. | Back porch will flow from the parallel connected transformer which may over-heat and eventually its insulation / winding failure may occur. Continuous back porch not available to single SCR gate. SCR may turn on for first half-cycle only due to pulse current. SCR will be turned off for remaining half-cycles. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 3 | Over Current. De-gradation of components. | 4 parallel SCRs in either direction to ensure loss of a single SCR will not endanger VSLs and other SCRs. | 2 | 6 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. |  | 3 | 18 | "In Bypass Telemetry field 'SCR and Clamp Board Status' will show following: SCR 1 (Output Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 2 (Mid 1 Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 3 (Mid 2 Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 4 (Input Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) | None. | Alert to be generated for the user to communicate the failure of one portion of SCR triggering path. | make two cases with single transformer winding failure and both transformers' winding failure PS19 Q&PI: Updated Second review: Second review IF one transformer fails, Back porch will flow from the parallel connected transformer which may over heat and eventually fail insulation/ winding failure may occur over time PLEASE update other columns PS19 Q&PI: Updated | [7 empty] | -1372
SV104-9787 |  |  |  | Both transformers winding failure. | Continuous back porch not available to single SCR gate. SCR may turn on for first half-cycle only due to pulse current. SCR will be turned off for remaining half-cycles. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 3 | Over Current. De-gradation of components. | 4 parallel SCRs in either direction to ensure loss of a single SCR will not endanger VSLs and other SCRs. | 2 | 6 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. |  | 3 | 18 | "In Bypass Telemetry field 'SCR and Clamp Board Status' will show following: SCR 1 (Output Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 2 (Mid 1 Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 3 (Mid 2 Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 4 (Input Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) | None. | Alert to be generated for the user to communicate the failure of one portion of SCR triggering path. | [8 empty] | -9787
SV104-13668 | Continuous Back Porch Current Driver Circuit - Transformers Output Diodes. | D6, D11, D21, D26, D36, D41, D51, D56, D66, D71 | To prevent reverse current from complementary circuit. | Diode fails short. | Overcurrent will eventually cause the diode to fail-open. Reverse current will cause over loading of windings. One half of the complementary circuit may degrade. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 3 | Over Current. De-gradation of components. | 4 parallel SCRs in either direction to ensure loss of a single SCR will not endanger VSLs and other SCRs. | 2 | 6 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | None. | 5 | 30 | None. | None. | [9 empty] | 13668
SV104-13669 |  |  |  | Both diodes fail short. | Back porch will flow from the parallel connected transformer which may over-heat and eventually its insulation / winding failure may occur. Continuous back porch not available to single SCR gate. SCR may turn on for first half-cycle only due to pulse current. SCR will be turned off for remaining half-cycles. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 3 | Over Current. De-gradation of components. | 4 parallel SCRs in either direction to ensure loss of a single SCR will not endanger VSLs and other SCRs. | 2 | 6 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. |  | 3 | 18 | "In Bypass Telemetry field 'SCR and Clamp Board Status' will show following: SCR 1 (Output Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 2 (Mid 1 Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 3 (Mid 2 Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 4 (Input Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) | None. | [9 empty] | 13669
SV104-13670 |  |  |  | Diode fails open. | Continuous back porch not available from one complementary circuit. SCR may turn on due to complementary circuit current. Transformer may over-heat and eventually its insulation / winding failure may occur. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 3 | Over Current. De-gradation of components. | 4 parallel SCRs in either direction to ensure loss of a single SCR will not endanger VSLs and other SCRs. | 2 | 6 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. |  | 3 | 18 | "In Bypass Telemetry field 'SCR and Clamp Board Status' will show following: SCR 1 (Output Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 2 (Mid 1 Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 3 (Mid 2 Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 4 (Input Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) | None. | [9 empty] | 13670
SV104-13671 |  |  |  | Both diodes fail open. | Continuous back porch not available to single SCR gate. SCR may turn on for first half-cycle only due to pulse current. SCR will be turned off for remaining half-cycles. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 3 | Over Current. De-gradation of components. | 4 parallel SCRs in either direction to ensure loss of a single SCR will not endanger VSLs and other SCRs. | 2 | 6 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. |  | 3 | 18 | "In Bypass Telemetry field 'SCR and Clamp Board Status' will show following: SCR 1 (Output Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 2 (Mid 1 Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 3 (Mid 2 Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 4 (Input Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) | None. | [9 empty] | 13671
SV104-13672 | Continuous Back Porch Current Driver Circuit - Transformers Auxiliary Grounding Diodes | D9, D13, D24, D28, D39, D43, D54, D58, D69, D73 | To prevent reverse current from ground. | Diode fails short. | No immediate effect. Prolong reverse current flow from ground may cause damage to the transformer windings. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 2 | Over Current. De-gradation of components. | Usage of over-rated components. | 2 | 4 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | None. | 5 | 20 | None. | None. | [9 empty] | 13672
SV104-13673 |  |  |  | Diode fails open. | No immediate effect. Isolation of windings may get affected. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 1 | Over Current. De-gradation of components. | Usage of over-rated components. | 1 | 1 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | None. | 5 | 5 | None. | None. | [9 empty] | 13673
SV104-1373 | Continuous Back Porch Current Driver Circuit - TVS Didoes. | D7, D12, D22, D27, D37, D42, D52, D57, D67, D72 | Transient Protection. | Diode fails-open. | Protection from transients will be reduced. Transformer may get saturated in case severe transients occurs. One SCR cannot trigger past first cycle in worst case. Under normal working conditions there will be no immediate effect. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 3 | High voltage transients | 4 parallel SCRs in either direction to ensure loss of a single SCR will not endanger VSLs and other SCRs. | 2 | 6 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. |  | 3 | 18 | "In Bypass Telemetry field 'SCR and Clamp Board Status' will show following: SCR 1 (Output Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 2 (Mid 1 Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 3 (Mid 2 Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 4 (Input Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) | None. | Alert to be generated for the user to communicate the failure of one portion of SCR triggering path. | Add a diode fail short case PS19 Q&PI: Updated | [7 empty] | -1373
SV104-9788 |  |  |  | Diode fails-short.. | Corresponding transformer's winding will be shorted. Back porch will flow from the parallel connected transformer which may over-heat and eventually its insulation / winding failure may occur. Continuous back porch not available to single SCR gate. SCR may turn on for first half-cycle only due to pulse current. SCR will be turned off for remaining half-cycles. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 3 | Over Current. De-gradation of components. | 4 parallel SCRs in either direction to ensure loss of a single SCR will not endanger VSLs and other SCRs. | 2 | 6 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. |  | 3 | 18 | "In Bypass Telemetry field 'SCR and Clamp Board Status' will show following: SCR 1 (Output Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 2 (Mid 1 Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 3 (Mid 2 Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 4 (Input Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) | None. | Alert to be generated for the user to communicate the failure of one portion of SCR triggering path. | Back porch will flow from the parallel connected transformer which may over heat and eventually fail insulation/ winding failure may occur over time PLEASE update other columns PS19 Q&PI: Updated | [7 empty] | -9788
SV104-1374 | Continuous Back Porch Current Driver Circuit - Drive Transistor. | Q4, Q5, Q9, Q10, Q12, Q15, Q19, Q20, Q24, Q25 | To enable constant current flow through the transformer. | Both transistors fails-short. | There will be an initial back porch pulse after which back porch current will not be available. During the shorting event if the pulse current is enough to latch the SCR, system may transit to monitoring mode. | If device was in injection mode it will switch to monitoring mode. Device will remain in Monitoring mode as long as this issue persists. | Affected device and its associated group of devices will transit to monitoring mode. System will keep working with reduced injection capability. | 4 | Over Current. De-gradation of components. | Usage of overrated components. | 2 | 8 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | SCR current measurement from Rogowski coil. | 2 | 16 | In Bypass Telemetry field 'SCR and Clamp Board Status' will show following: SCR 1 (Output Side): Two SCRs Fired OR SCR 2 (Mid 1 Side): Two SCRs Fired OR SCR 3 (Mid 2 Side): Two SCRs Fired OR SCR 4 (Input Side): Two SCRs Fired | On SmartInterface following Alarm will be raised: If SCR > 100 SCR Failed Short If Line Current > 80A && SCR firing duration = 10 mins SCR Prolong Firing | Alert to be generated for the user to communicate the failure of one portion of SCR triggering path. | There will be an initial back porch pulse after which back porch current will not be available. During the shorting event if the pulse current is enough to latch the SCR, system may transit to monitoring mode PS19 Q&PI: same is already mentioned | [7 empty] | -1374
SV104-1375 |  |  |  | Single Transistor fails-open. | Continuous back porch will flow from parallel connected transformer. Back porch will flow from the parallel connected transformer which may over-heat and eventually insulation / winding failure may occur over time. During the shorted duration if the pulse current is enough to latch the SCR, system may transit to monitoring mode | If device was in injection mode it will switch to monitoring mode. Device will remain in Monitoring mode as long as this issue persists. | Affected device and its associated group of devices will transit to monitoring mode. System will keep working with reduced injection capability. | 4 | Over Current. De-gradation of components. | Usage of overrated components. | 2 | 8 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | SCR current measurement from Rogowski coil. | 2 | 16 | In Bypass Telemetry field 'SCR and Clamp Board Status' will show following: SCR 1 (Output Side): Two SCRs Fired OR SCR 2 (Mid 1 Side): Two SCRs Fired OR SCR 3 (Mid 2 Side): Two SCRs Fired OR SCR 4 (Input Side): Two SCRs Fired | On SmartInterface following Alarm will be raised: If SCR > 100 SCR Failed Short If Line Current > 80A && SCR firing duration = 10 mins SCR Prolong Firing | Alert to be generated for the user to communicate the failure of one portion of SCR triggering path. | Back porch will flow from the parallel connected transformer which may over heat and eventually fail insulation/ winding failure may occur over time leading to the case mentioned in row 114. During the shorting event if the pulse current is enough to latch the SCR, system may transit to monitoring mode PS19 Q&PI: Updated Second review UPDATE OTHER COLUMNS ACCORDINGLY for example if SCR gets latched, system will transit to monitoring mode PS19 Q&PI: updated | [7 empty] | -1375
SV104-1376 |  |  |  | Both Transistors fails-open. | Continuous back porch not available to single SCR gate. SCR may turn on for first half-cycle only due to pulse current. SCR will be turned off for remaining half-cycles. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 3 | High voltage transients | 4 parallel SCRs in either direction to ensure loss of a single SCR will not endanger VSLs and other SCRs. | 2 | 6 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. |  | 3 | 18 | "In Bypass Telemetry field 'SCR and Clamp Board Status' will show following: SCR 1 (Output Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 2 (Mid 1 Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 3 (Mid 2 Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 4 (Input Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) | None. | [9 empty] | -1376
SV104-1377 | Continuous Back Porch Current Driver Circuit - IC Gate Driver. | U1, U3, U10, U12, U19, U21, U28, U30, U37, U39 | To drive gate current of drive transistor. | Input side Resistor fails-open | Continuous back porch will flow from parallel connected transformer. Remaining parallel connected transformer may over heat and eventually fail-open. Single SCR may turn on for first half-cycle only due to pulse current. Single SCR will be turned off for remaining half-cycles in worst case. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 3 | High voltage transients | 4 parallel SCRs in either direction to ensure loss of a single SCR will not endanger VSLs and other SCRs. | 2 | 6 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. |  | 3 | 18 | "In Bypass Telemetry field 'SCR and Clamp Board Status' will show following: SCR 1 (Output Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 2 (Mid 1 Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 3 (Mid 2 Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 4 (Input Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) | None. |  | Continuous back porch will flow from parallel connected transformer. Remaining parallel connected transformer may over heat and eventually its winding failure may occur. Single SCR may turn on for first half-cycle only due to pulse current. Single SCR will be turned off for remaining half-cycles in worst case. Ps19 Q&PI: Updated | [7 empty] | -1377
SV104-1378 |  |  |  | Output side Resistor fails-open. | Continuous back porch will flow from parallel connected transformer. Remaining parallel connected transformer may over heat and eventually fail-open. Single SCR may turn on for first half-cycle only due to pulse current. Single SCR will be turned off for remaining half-cycles in worst case. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 3 | High voltage transients | 4 parallel SCRs in either direction to ensure loss of a single SCR will not endanger VSLs and other SCRs. | 2 | 6 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. |  | 3 | 18 | "In Bypass Telemetry field 'SCR and Clamp Board Status' will show following: SCR 1 (Output Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 2 (Mid 1 Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 3 (Mid 2 Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 4 (Input Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) | None. |  | Continuous back porch will flow from parallel connected transformer. Remaining parallel connected transformer may over heat and eventually its winding failure may occur. Single SCR may turn on for first half-cycle only due to pulse current. Single SCR will be turned off for remaining half-cycles in worst case. Ps19 Q&PI: Updated | [7 empty] | -1378
SV104-13674 | Continuous Back Porch Current Driver Circuit - Gate Driver IC Input Resistor | R7, R14, R41, R48, R75, R82, R109, R116, R143, R150 | To provide input signal to gate driver IC. | Resistor fails short. | No immediate effect. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 1 | Over Current. De-gradation of components. | Usage of over-rated components. | 1 | 1 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | None. | 5 | 5 | None. | None. | [9 empty] | 13674
SV104-13675 |  |  |  | Resistor fails open. | Gate driver IC will not trigger MOSFET. Continuous back porch will flow from parallel connected transformer. Remaining parallel connected transformer may over heat and eventually fail-open. Single SCR may turn on for first half-cycle only due to pulse current. Single SCR will be turned off for remaining half-cycles in worst case. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 3 | High voltage transients | 4 parallel SCRs in either direction to ensure loss of a single SCR will not endanger VSLs and other SCRs. | 1 | 3 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. |  | 3 | 9 | "In Bypass Telemetry field 'SCR and Clamp Board Status' will show following: SCR 1 (Output Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 2 (Mid 1 Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 3 (Mid 2 Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 4 (Input Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) | None. | [9 empty] | 13675
SV104-13676 | Continuous Back Porch Current Driver Circuit - Gate Driver IC Output Voltage Divider Resistors | R9, R16, R43, R50, R77, R84, R111, R118, R145, R152, R154, R213, R258, R259, R260, R261, R359, R360, R361, R362, | To provide biasing voltage for the transistor. | Resistor fails short. | Overvoltage at gate may saturate MOSFET. Constant high at MOSFET output. Continuous back porch will flow from parallel connected transformer. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 1 | Over Current. De-gradation of components. | Usage of over-rated components. | 1 | 1 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | None. | 5 | 5 | None. | None. | [9 empty] | 13676
SV104-13677 |  |  |  | Resistor fails open. | MOSFET will not trigger. Continuous back porch will flow from parallel connected transformer. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 1 | Over Current. De-gradation of components. | Usage of over-rated components. | 1 | 1 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | None. | 5 | 5 | None. | None. | [9 empty] | 13677
SV104-1379 | Continuous Back Porch Current Driver Circuit - Hall Effect Sensor Input Side Inductor. | L1, L2, L3, L4, L5 | To suppress noise. | Inductor fails-open. | Continuous back porch not available to single SCR gate. SCR may turn on for first half-cycle only due to pulse current. SCR will be turned off for remaining half-cycles. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 3 | High voltage transients | 4 parallel SCRs in either direction to ensure loss of a single SCR will not endanger VSLs and other SCRs. | 1 | 3 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. |  | 3 | 9 | "In Bypass Telemetry field 'SCR and Clamp Board Status' will show following: SCR 1 (Output Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 2 (Mid 1 Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 3 (Mid 2 Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 4 (Input Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) | None. | [9 empty] | -1379
SV104-5112 |  |  |  | Inductor fails-short. | No immediate effect. Filtration will be reduced. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 2 | High voltage transients | 4 parallel SCRs in either direction to ensure loss of a single SCR will not endanger VSLs and other SCRs. | 1 | 2 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | None. | 5 | 10 | None. | None. |  | This a not a case worth considering. Shorting of filter inductor is not a big issue. | [7 empty] | -5112
SV104-1380 | Continuous Back Porch Current Driver Circuit - Hall Effect Sensor Output Side Diode. | D8, D23, D38, D53, D68 | Reverse Current Protection. | Diode fails-open. | Continuous back porch not available to single SCR gate. SCR may turn on for first half-cycle only due to pulse current. SCR will be turned off for remaining half-cycles. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 3 | High voltage transients | 4 parallel SCRs in either direction to ensure loss of a single SCR will not endanger VSLs and other SCRs. | 2 | 6 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. |  | 3 | 18 | "In Bypass Telemetry field 'SCR and Clamp Board Status' will show following: SCR 1 (Output Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 2 (Mid 1 Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 3 (Mid 2 Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 4 (Input Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) | None. | [9 empty] | -1380
SV104-1381 | Continuous Back Porch Current Driver Circuit - Hall Effect Sensor. | U4, U13, U22, U31, U40 | To measure current for regulation and feedback. | IC failure. | Continuous back porch not available to single SCR gate. SCR will turn on for first half-cycle only due to pulse current. SCR will be turned off for remaining half-cycles. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 3 | High voltage transients | 4 parallel SCRs in either direction to ensure loss of a single SCR will not endanger VSLs and other SCRs. | 2 | 6 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. |  | 3 | 18 | "In Bypass Telemetry field 'SCR and Clamp Board Status' will show following: SCR 1 (Output Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 2 (Mid 1 Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 3 (Mid 2 Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 4 (Input Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) | None. | [9 empty] | -1381
SV104-13678 | Current Sense RC Filter | R17, R85, R119, R151, R153, C6, C23, C40, C57, C74 | To filter noise. | Resistor fails open. | Current Sensing Signal will not be available. At the start of SCR firing Hall effect sensor delay will not be compensated. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 3 | High voltage transients | 4 parallel SCRs in either direction to ensure loss of a single SCR will not endanger VSLs and other SCRs. | 1 | 3 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | None. | 5 | 15 | None. | None. | [9 empty] | 13678
SV104-13679 |  |  |  | Capacitor fails short. | Current Sense signal shorted to ground. Current Sensing Signal will not be available. At the start of SCR firing Hall effect sensor delay will not be compensated. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 3 | High voltage transients | 4 parallel SCRs in either direction to ensure loss of a single SCR will not endanger VSLs and other SCRs. | 1 | 3 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | None. | 5 | 15 | None. | None. | [9 empty] | 13679
SV104-1382 | Continuous Back Porch Current Regulation Circuit - Comparator - Current Sense Reference Series Divider. | R21, R22, R26, R27, R55, R56, R60, R61, R89, R90, R94, R95, R123, R124, R128, R129, R157, R158, R162, R163 | Provide Reference current. | Resistor fails-open. | Continuous back porch current regulation will be affected. Single SCR may remain off except for first half cycle. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 3 | High voltage transients | 4 parallel SCRs in either direction to ensure loss of a single SCR will not endanger VSLs and other SCRs. | 1 | 3 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | On board SCR gate current measurement. | 3 | 9 | "In Bypass Telemetry field 'SCR and Clamp Board Status' will show following: SCR 1 (Output Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 2 (Mid 1 Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 3 (Mid 2 Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 4 (Input Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) | None. | [9 empty] | -1382
SV104-5113 |  |  |  | Resistor fails-short. | Overcurrent will cause the resistor to eventually fail-open. Continuous back porch current regulation will be affected. Single SCR may remain off except for first half cycle. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 3 | High voltage transients | 4 parallel SCRs in either direction to ensure loss of a single SCR will not endanger VSLs and other SCRs. | 1 | 3 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | On board SCR gate current measurement. | 3 | 9 | "In Bypass Telemetry field 'SCR and Clamp Board Status' will show following: SCR 1 (Output Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 2 (Mid 1 Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 3 (Mid 2 Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 4 (Input Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) | None. | [9 empty] | -5113
SV104-1383 | Continuous Back Porch Current Regulation Circuit - Comparator - Current Sense Reference Series Divider - Decoupling Capacitor. | C11, C12, C28, C29, C45, C46, C62, C63, C79, C80 | To suppress noise. | Capacitor fails-open. | Continuous back porch current regulation will be affected. Single SCR may remain off except for first half cycle. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 3 | Over Current. De-gradation of components. | Usage of over-rated components. | 1 | 3 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. |  | 3 | 9 | "In Bypass Telemetry field 'SCR and Clamp Board Status' will show following: SCR 1 (Output Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 2 (Mid 1 Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 3 (Mid 2 Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 4 (Input Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) | None. | [9 empty] | -1383
SV104-5114 |  |  |  | Capacitor fails-short. | Overcurrent will cause the capacitor to eventually fail-open. Continuous back porch current regulation will be affected. Single SCR may remain off except for first half cycle. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 3 | Over Current. De-gradation of components. | Usage of over-rated components. | 1 | 3 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. |  | 3 | 9 | "In Bypass Telemetry field 'SCR and Clamp Board Status' will show following: SCR 1 (Output Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 2 (Mid 1 Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 3 (Mid 2 Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 4 (Input Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) | None. | [9 empty] | -5114
SV104-1384 | Continuous Back Porch Current Regulation Circuit - Comparator. | U5, U14, U23, U32, U41 | Compare SCR gate current with reference. | IC failure. | Continuous back porch current regulation will be affected. Single SCR may remain off except for first half cycle. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 3 | Over Current. De-gradation of components. | Usage of over-rated components. | 2 | 6 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. |  | 3 | 18 | "In Bypass Telemetry field 'SCR and Clamp Board Status' will show following: SCR 1 (Output Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 2 (Mid 1 Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 3 (Mid 2 Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 4 (Input Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) | None. | [9 empty] | -1384
SV104-1385 | Continuous Back Porch Current Regulation Circuit - Flip Flop. | U6, U9, U15, U18, U24, U27, U33, U36, U42, U45 | Configure dead time control for PWM controller based on SCR Gate current sensing. | IC failure. | Continuous back porch current regulation will be affected. Single SCR may remain off except for first half cycle. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 3 | Over Current. De-gradation of components. | Usage of over-rated components. | 2 | 6 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. |  | 3 | 18 | "In Bypass Telemetry field 'SCR and Clamp Board Status' will show following: SCR 1 (Output Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 2 (Mid 1 Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 3 (Mid 2 Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 4 (Input Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) | None. | [9 empty] | -1385
SV104-1386 | Continuous Back Porch Current Regulation Circuit - Flip Flop - Series Resistor In Connection To PWM Controller. | R23, R57, R91, R125, R159 |  | Resistor fails-open. | Continuous back porch current regulation will be affected. Single SCR may remain off except for first half cycle. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 3 | Over Current. De-gradation of components. | Usage of over-rated components. | 1 | 3 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. |  | 3 | 9 | "In Bypass Telemetry field 'SCR and Clamp Board Status' will show following: SCR 1 (Output Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 2 (Mid 1 Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 3 (Mid 2 Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 4 (Input Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) | None. | [9 empty] | -1386
SV104-5115 |  |  |  | Resistor fails-short. | Overcurrent will cause the resistor to eventually fail-open. Continuous back porch current regulation will be affected. Single SCR may remain off except for first half cycle. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 3 | Over Current. De-gradation of components. | Usage of over-rated components. | 1 | 3 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. |  | 3 | 9 | "In Bypass Telemetry field 'SCR and Clamp Board Status' will show following: SCR 1 (Output Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 2 (Mid 1 Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 3 (Mid 2 Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 4 (Input Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) | None. | [9 empty] | -5115
SV104-1387 | Continuous Back Porch Current Regulation Circuit - Diodes In Connection To PWM Controller. | D14, D15, D29, D30, D44, D45, D59, D60, D74, D75, D107, D108, D109, D110, D111, D133, D134, D135, D136, D137 | To set dead time control of PWM controller . | Diode fails-open. | Continuous back porch current regulation will be affected. Single SCR may remain off except for first half cycle. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 3 | Over Current. De-gradation of components. | Usage of over-rated components. | 2 | 6 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. |  | 3 | 18 | "In Bypass Telemetry field 'SCR and Clamp Board Status' will show following: SCR 1 (Output Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 2 (Mid 1 Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 3 (Mid 2 Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 4 (Input Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) | None. | [9 empty] | -1387
SV104-5116 |  |  |  | Diode fails-short. | Overcurrent will cause the diode to eventually fail-open. Continuous back porch current regulation will be affected. Single SCR may remain off except for first half cycle. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 3 | Over Current. De-gradation of components. | Usage of over-rated components. | 2 | 6 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. |  | 3 | 18 | "In Bypass Telemetry field 'SCR and Clamp Board Status' will show following: SCR 1 (Output Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 2 (Mid 1 Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 3 (Mid 2 Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 4 (Input Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) | None. | [9 empty] | -5116
SV104-1388 | Continuous Back Porch Current Regulation Circuit - PWM Controller - Oscillator Frequency Components. | C13, C15, C30, C32, C47, C49, C64, C66, C81, C83, C272, C273, C274, C275, C276 | Set Oscillator frequency. | Capacitor fails-open. | Continuous back porch not available to single SCR gate. SCR may turn on for first half-cycle only due to pulse current. SCR will be turned off for remaining half-cycles. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 3 | High voltage transients | 4 parallel SCRs in either direction to ensure loss of a single SCR will not endanger VSLs and other SCRs. | 1 | 3 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | On board SCR gate current measurement. | 3 | 9 | "In Bypass Telemetry field 'SCR and Clamp Board Status' will show following: SCR 1 (Output Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 2 (Mid 1 Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 3 (Mid 2 Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 4 (Input Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) | None. | [9 empty] | -1388
SV104-5117 |  |  |  | Capacitor fails-short. | Overcurrent will cause the resistor to eventually fail-open. Continuous back porch not available to single SCR gate. SCR may turn on for first half-cycle only due to pulse current. SCR will be turned off for remaining half-cycles. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 3 | High voltage transients | 4 parallel SCRs in either direction to ensure loss of a single SCR will not endanger VSLs and other SCRs. | 1 | 3 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | On board SCR gate current measurement. | 3 | 9 | "In Bypass Telemetry field 'SCR and Clamp Board Status' will show following: SCR 1 (Output Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 2 (Mid 1 Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 3 (Mid 2 Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 4 (Input Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) | None. | [9 empty] | -5117
SV104-1389 |  | R28, R29, R31, R32, R397, R62, R63, R64, R65, R66, R96, R97, R98, R99, R100, R130, R131, R132, R133, R134, R165, R166, R167, R168, R177, R398, R399, R400, R401, R2164 |  | Resistor fails-open. | Continuous back porch not available to single SCR gate. SCR may turn on for first half-cycle only due to pulse current. SCR will be turned off for remaining half-cycles. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 3 | High voltage transients | 4 parallel SCRs in either direction to ensure loss of a single SCR will not endanger VSLs and other SCRs. | 1 | 3 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | On board SCR gate current measurement. | 3 | 9 | "In Bypass Telemetry field 'SCR and Clamp Board Status' will show following: SCR 1 (Output Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 2 (Mid 1 Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 3 (Mid 2 Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 4 (Input Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) | None. | [9 empty] | -1389
SV104-5118 |  |  |  | Resistor fails-short. | Overcurrent will cause the resistor to eventually fail-open. Continuous back porch not available to single SCR gate. SCR may turn on for first half-cycle only due to pulse current. SCR will be turned off for remaining half-cycles. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 3 | High voltage transients | 4 parallel SCRs in either direction to ensure loss of a single SCR will not endanger VSLs and other SCRs. | 1 | 3 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | On board SCR gate current measurement. | 3 | 9 | "In Bypass Telemetry field 'SCR and Clamp Board Status' will show following: SCR 1 (Output Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 2 (Mid 1 Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 3 (Mid 2 Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 4 (Input Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) | None. | [9 empty] | -5118
SV104-5119 |  |  |  | Resistor fails-short. | Overcurrent will cause the resistor to eventually fail-open. Continuous back porch not available to single SCR gate. SCR may turn on for first half-cycle only due to pulse current. SCR will be turned off for remaining half-cycles. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 3 | High voltage transients | 4 parallel SCRs in either direction to ensure loss of a single SCR will not endanger VSLs and other SCRs. | 1 | 3 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | On board SCR gate current measurement. | 3 | 9 | "In Bypass Telemetry field 'SCR and Clamp Board Status' will show following: SCR 1 (Output Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 2 (Mid 1 Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 3 (Mid 2 Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 4 (Input Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) | None. | [9 empty] | -5119
SV104-1390 | Continuous Back Porch Current Regulation Circuit - PWM Controller - Error Amplifier Feedback Resistors. | R24, R58, R92, R126, R160, R218, R219, R220, R221, R222 | Provide gate current feedback. | Resistor fails-open. | Continuous back porch current regulation will be affected. Single SCR may remain off except for first half cycle. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 3 | High voltage transients | 4 parallel SCRs in either direction to ensure loss of a single SCR will not endanger VSLs and other SCRs. | 1 | 3 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | On board SCR gate current measurement. | 3 | 9 | "In Bypass Telemetry field 'SCR and Clamp Board Status' will show following: SCR 1 (Output Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 2 (Mid 1 Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 3 (Mid 2 Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 4 (Input Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) | None. | [9 empty] | -1390
SV104-5120 |  |  |  | Resistor fails-short. | Overcurrent will cause the resistor to eventually fail-open. Continuous back porch current regulation will be affected. Single SCR may remain off except for first half cycle. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 3 | High voltage transients | 4 parallel SCRs in either direction to ensure loss of a single SCR will not endanger VSLs and other SCRs. | 1 | 3 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | On board SCR gate current measurement. | 3 | 9 | "In Bypass Telemetry field 'SCR and Clamp Board Status' will show following: SCR 1 (Output Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 2 (Mid 1 Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 3 (Mid 2 Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 4 (Input Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) | None. | [9 empty] | -5120
| SCR Gate Driver Board - CTP Volt Level Detector & One Shot Circuit | [26 empty] | 0
SV104-1392 | 12 V Regulator Circuit - Zener Diode. | D2, D32, D62, D78, D80 | To provide power to the components. | Diode fails-open. | 30 V will be produced at the output which will damage on-board electronics. Loss of gate current for a single SCR. Remaining SCRs will see a higher current during fault and transition in one direction only. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 3 | Over Current. De-gradation of components. | Usage of over-rated components. | 2 | 6 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | On board SCR gate current measurement. | 3 | 18 | "In Bypass Telemetry field 'SCR and Clamp Board Status' will show following: SCR 1 (Output Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 2 (Mid 1 Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 3 (Mid 2 Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 4 (Input Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) | None. | Alert to be generated for the user to communicate the failure of one portion of SCR triggering path. | 30 volt will be produced at the output which will damage on board electronics and thus loss of gate current for one SCR. Remaining SCRs will see a higher current during fault and transition in one direction only. PS19 Q&PI: Updated | [7 empty] | -1392
SV104-5121 |  |  |  | Diode fails-short. | Overcurrent will eventually cause the diode to fail-open. No power to on-board electronics for Gate current of single SCR. Loss of gate current for a single SCR. Remaining SCRs will see a higher current during fault and transition in one direction only. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 3 | Over Current. De-gradation of components. | Usage of over-rated components. | 2 | 6 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | On board SCR gate current measurement. | 3 | 18 | "In Bypass Telemetry field 'SCR and Clamp Board Status' will show following: SCR 1 (Output Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 2 (Mid 1 Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 3 (Mid 2 Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 4 (Input Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) | None. | Alert to be generated for the user to communicate the failure of one portion of SCR triggering path. | [8 empty] | -5121
SV104-1393 | 12 V Regulator Circuit - Darlington Pair. | Q33, Q34, Q51, Q53, Q55, Q57, Q58, Q60, Q62, Q64 | To provide high current gain. | Transistor fails-open. | No power to on-board electronics for Gate current of single SCR. Loss of gate current for a single SCR. Remaining SCRs will see a higher current during fault and transition in one direction only. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 3 | Over Current. De-gradation of components. | Usage of over-rated components. | 2 | 6 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | On board SCR gate current measurement. | 3 | 18 | "In Bypass Telemetry field 'SCR and Clamp Board Status' will show following: SCR 1 (Output Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 2 (Mid 1 Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 3 (Mid 2 Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 4 (Input Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) | None. | Alert to be generated for the user to communicate the failure of one portion of SCR triggering path. | [8 empty] | -1393
SV104-5122 |  |  |  | Transistor fails-short. | No power to on-board electronics for Gate current of single SCR. Loss of gate current for a single SCR. Remaining SCRs will see a higher current during fault and transition in one direction only. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 3 | Over Current. De-gradation of components. | Usage of over-rated components. | 2 | 6 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | On board SCR gate current measurement. | 3 | 18 | "In Bypass Telemetry field 'SCR and Clamp Board Status' will show following: SCR 1 (Output Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 2 (Mid 1 Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 3 (Mid 2 Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 4 (Input Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) | None. | Alert to be generated for the user to communicate the failure of one portion of SCR triggering path. | [8 empty] | -5122
SV104-1394 | 12 V Regulator Circuit - Output Capacitor. | C16, C34, C67, C84, C150 | To provide smooth output. | Capacitor fails-open. | No immediate effect. Noise at output may cause on-board electronics to malfunction. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 1 | Over Voltage De-gradation of components. | Usage of over-rated components. | 1 | 1 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | None. | 5 | 5 | None. | None. | Alert to be generated for the user to communicate the failure of one portion of SCR triggering path. | [8 empty] | -1394
SV104-5123 |  |  |  | Capacitor fails-short. | 12 V supply will not be available till the time capacitor remains shorted. Over current will cause the capacitor to eventually fail-open. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 1 | Over Voltage De-gradation of components. | Usage of over-rated components. | 1 | 1 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | None. | 5 | 5 | None. | None. | Alert to be generated for the user to communicate the failure of one portion of SCR triggering path. | [8 empty] | -5123
SV104-1395 | 12 V Regulator Circuit - Current Bias Resistor. | R33, R67, R151, R186, R195 | Provide adequate current to ensure transistor's gain. | Resistor fails-open. | No power to on-board electronics for Gate current of single SCR. Loss of gate current for a single SCR. Remaining SCRs will see a higher current during fault and transition in one direction only. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 3 | Over Current. De-gradation of components. | Usage of over-rated components. | 1 | 3 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | On board SCR gate current measurement. | 3 | 9 | "In Bypass Telemetry field 'SCR and Clamp Board Status' will show following: SCR 1 (Output Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 2 (Mid 1 Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 3 (Mid 2 Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 4 (Input Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) | None. | Alert to be generated for the user to communicate the failure of one portion of SCR triggering path. | [8 empty] | -1395
SV104-5124 |  |  |  | Resistor fails-short. | Overcurrent will cause the resistor to eventually fail-open. No power to on-board electronics for Gate current of single SCR. Loss of gate current for a single SCR. Remaining SCRs will see a higher current during fault and transition in one direction only. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 3 | Over Current. De-gradation of components. | Usage of over-rated components. | 1 | 3 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | On board SCR gate current measurement. | 3 | 9 | "In Bypass Telemetry field 'SCR and Clamp Board Status' will show following: SCR 1 (Output Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 2 (Mid 1 Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 3 (Mid 2 Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 4 (Input Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) | None. | Alert to be generated for the user to communicate the failure of one portion of SCR triggering path. | [8 empty] | -5124
SV104-1396 | 12 V Regulator Circuit - Current Limiting Resistor At Base Of Darlington Pair. | R34, R42, R101, R117, R164, R170, R188, R190, R197, R199 | To limit current flow in the transistor. | Resistor fails-open. | No power to on-board electronics for Gate current of single SCR. Loss of gate current for a single SCR. Remaining SCRs will see a higher current during fault and transition in one direction only. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 3 | Over Current. De-gradation of components. | Usage of over-rated components. | 1 | 3 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | On board SCR gate current measurement. | 3 | 9 | "In Bypass Telemetry field 'SCR and Clamp Board Status' will show following: SCR 1 (Output Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 2 (Mid 1 Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 3 (Mid 2 Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 4 (Input Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) | None. | Alert to be generated for the user to communicate the failure of one portion of SCR triggering path. | [8 empty] | -1396
SV104-5125 |  |  |  | Resistor fails-short. | No immediate effect. There is not enough current to cause opening of this resistor. Transistor degradation could occur leading to its failure. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 2 | Over Current. De-gradation of components. | Usage of over-rated components. | 1 | 2 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | On board SCR gate current measurement. | 3 | 6 | "In Bypass Telemetry field 'SCR and Clamp Board Status' will show following: SCR 1 (Output Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 2 (Mid 1 Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 3 (Mid 2 Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 4 (Input Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) | None. | Alert to be generated for the user to communicate the failure of one portion of SCR triggering path. | No immediate effect. There is not enough current to cause opening of this resistor. Transistor degradation could occur leading to its failure. PS19 Q&PI: Updated | [7 empty] | -5125
SV104-1397 | 12 V Regulator Circuit - Voltage Compensation Diode. | D98, D100, D102, D104, D106 | To compensate for voltage drop across BJTs. | Diode fails-open. | 30 V will be produced at the output which will damage on-board electronics. Loss of gate current for a single SCR. Remaining SCRs will see a higher current during fault and transition in one direction only. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 3 | Over Current. De-gradation of components. | Usage of over-rated components. | 2 | 6 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | On board SCR gate current measurement. | 3 | 18 | "In Bypass Telemetry field 'SCR and Clamp Board Status' will show following: SCR 1 (Output Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 2 (Mid 1 Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 3 (Mid 2 Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 4 (Input Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) | None. | Alert to be generated for the user to communicate the failure of one portion of SCR triggering path. | 30 volt will be produced at the output which will damage on board electronics and thus loss of gate current for one SCR. Remaining SCRs will see a higher current during fault and transition in one direction only. PS19 Q&PI: Updated | [7 empty] | -1397
SV104-5126 |  |  |  | Diode fails-short. | No immediate effect. There is not enough current to cause opening of diode, so only voltage compensation will be lost and less then 12 V will be produced affecting the operation of SCR gate current circuit to some extent. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 2 | Over Current. De-gradation of components. | Usage of over-rated components. | 2 | 4 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | On board SCR gate current measurement. | 3 | 12 | "In Bypass Telemetry field 'SCR and Clamp Board Status' will show following: SCR 1 (Output Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 2 (Mid 1 Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 3 (Mid 2 Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 4 (Input Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) | None. | Alert to be generated for the user to communicate the failure of one portion of SCR triggering path. | No immediate effect. There is not enough current to cause opening of this diode, so only voltage compensation will be lost and less then 12 V will be produced effecting the operation of SCR gate current circuit to some extant. PS19 Q&PI: Updated | [7 empty] | -5126
SV104-1398 | 12 V Regulator Circuit - Output Side Protection Diode. | D112, D121, D124, D125, D127 | To provide overvoltage protection. | Diode fails-open. | No immediate effect. Overvoltage protection for the circuit will be compromised. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 1 | Over Voltage De-gradation of components. | Usage of over-rated components. | 2 | 2 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | None. | 5 | 10 | None. | None. | Alert to be generated for the user to communicate the failure of one portion of SCR triggering path. | [8 empty] | -1398
SV104-5127 |  |  |  | Diode fails-short. | Overvoltage protection for the circuit will be compromised. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 1 | Over Voltage De-gradation of components. | Usage of over-rated components. | 2 | 2 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | None. | 5 | 10 | None. | None. | Alert to be generated for the user to communicate the failure of one portion of SCR triggering path. | [8 empty] | -5127
SV104-1399 | 5 V Regulator Circuit - Shunt Regulator. | U8, U17, U26, U35, U70 | To provide reference voltage. | IC failure. | No power to on-board electronics for Gate current of single SCR. Loss of gate current for a single SCR. Remaining SCRs will see a higher current during fault and transition in one direction only. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 3 | Over Current. De-gradation of components. | Usage of over-rated components. | 2 | 6 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | On board SCR gate current measurement. | 3 | 18 | "In Bypass Telemetry field 'SCR and Clamp Board Status' will show following: SCR 1 (Output Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 2 (Mid 1 Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 3 (Mid 2 Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 4 (Input Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) | None. | Alert to be generated for the user to communicate the failure of one portion of SCR triggering path. | [8 empty] | -1399
SV104-13680 | 5 V Regulator Circuit - 12V Zener Diode. | D17, D47, D77, D79, D81 | Overvoltage protection of shunt regulator. | Diode fails-open. | Shunt regulator protection is compromised. Overvoltage may cause shunt regulator failure. 5V supply is not available. | No power to on-board electronics for Gate current of single SCR. Loss of gate current for a single SCR. Remaining SCRs will see a higher current during fault and transition in one direction only. Device can operate in both injection and monitoring mode. | System will keep working normally. | 3 | Over Current. De-gradation of components. | Usage of over-rated components. | 2 | 6 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | On board SCR gate current measurement. | 3 | 18 | "In Bypass Telemetry field 'SCR and Clamp Board Status' will show following: SCR 1 (Output Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 2 (Mid 1 Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 3 (Mid 2 Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 4 (Input Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) | None. | [9 empty] | 13680
SV104-13681 |  |  |  | Diode fails-short. | Shunt regulator is bypassed. 5V supply is not available. | No power to on-board electronics for Gate current of single SCR. Loss of gate current for a single SCR. Remaining SCRs will see a higher current during fault and transition in one direction only. Device can operate in both injection and monitoring mode. | System will keep working normally. | 3 | Over Current. De-gradation of components. | Usage of over-rated components. | 2 | 6 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | On board SCR gate current measurement. | 3 | 18 | "In Bypass Telemetry field 'SCR and Clamp Board Status' will show following: SCR 1 (Output Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 2 (Mid 1 Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 3 (Mid 2 Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 4 (Input Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) | None. | [9 empty] | 13681
SV104-13682 | 5 V Regulator Circuit - Reference Voltage Capacitor. | C17, C50, C68, C142, C144 | To stabilize reference voltage of shunt regulator. | Capacitor fails-open. | No immediate effect. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 1 | Over Current. De-gradation of components. | Usage of over-rated components. | 1 | 1 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | None. | 5 | 5 | None. | None. | [9 empty] | 13682
SV104-13683 |  |  |  | Capacitor fails-short. | Shunt regulator reference gets shorted to cathode. Shunt regulator failure. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 2 | Over Current. De-gradation of components. | Usage of over-rated components. | 1 | 2 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | None. | 5 | 10 | None. | None. | [9 empty] | 13683
SV104-1400 | 5 V Regulator Circuit - Darlington Pair. | Q31, Q32, Q35, Q52, Q54, Q56, Q59, Q61, Q63, Q65 | To provide high current gain. | Transistor fails-open. | No power to on-board electronics for Gate current of single SCR. Loss of gate current for a single SCR. Remaining SCRs will see a higher current during fault and transition in one direction only. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 3 | Over Current. De-gradation of components. | Usage of over-rated components. | 2 | 6 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | On board SCR gate current measurement. | 3 | 18 | "In Bypass Telemetry field 'SCR and Clamp Board Status' will show following: SCR 1 (Output Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 2 (Mid 1 Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 3 (Mid 2 Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 4 (Input Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) | None. | Alert to be generated for the user to communicate the failure of one portion of SCR triggering path. | [8 empty] | -1400
SV104-5128 |  |  |  | Transistor fails-short. | Overcurrent will cause the transistor to fail-open. No power to on-board electronics for Gate current of single SCR. Loss of gate current for a single SCR. Remaining SCRs will see a higher current during fault and transition in one direction only. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 3 | Over Current. De-gradation of components. | Usage of over-rated components. | 2 | 6 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | On board SCR gate current measurement. | 3 | 18 | "In Bypass Telemetry field 'SCR and Clamp Board Status' will show following: SCR 1 (Output Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 2 (Mid 1 Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 3 (Mid 2 Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 4 (Input Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) | None. | Alert to be generated for the user to communicate the failure of one portion of SCR triggering path. | [8 empty] | -5128
SV104-1401 | 5 V Regulator Circuit - External Divider Circuit. | R76, R83, R102, R135, R169, R178, R191, R192, R200, R201 | To adjust output voltage of shunt regulator. | Resistor fails-open. | No power to on-board electronics for Gate current of single SCR. Loss of gate current for a single SCR. Remaining SCRs will see a higher current during fault and transition in one direction only. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 3 | Over Current. De-gradation of components. | Usage of over-rated components. | 1 | 3 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | On board SCR gate current measurement. | 3 | 9 | "In Bypass Telemetry field 'SCR and Clamp Board Status' will show following: SCR 1 (Output Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 2 (Mid 1 Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 3 (Mid 2 Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 4 (Input Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) | None. | Alert to be generated for the user to communicate the failure of one portion of SCR triggering path. | [8 empty] | -1401
SV104-5129 |  |  |  | Resistor fails-short. | Overcurrent will cause the resistor to fail-open. No power to on-board electronics for Gate current of single SCR. Loss of gate current for a single SCR. Remaining SCRs will see a higher current during fault and transition in one direction only. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 3 | Over Current. De-gradation of components. | Usage of over-rated components. | 1 | 3 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | On board SCR gate current measurement. | 3 | 9 | "In Bypass Telemetry field 'SCR and Clamp Board Status' will show following: SCR 1 (Output Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 2 (Mid 1 Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 3 (Mid 2 Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 4 (Input Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) | None. | Alert to be generated for the user to communicate the failure of one portion of SCR triggering path. | [8 empty] | -5129
SV104-1402 | 5 V Regulator Circuit - Current Bias Resistor. | R8, R49, R144, R187, R196 | Provide adequate current to ensure transistor's gain. | Resistor fails-open. | No power to on-board electronics for Gate current of single SCR. Loss of gate current for a single SCR. Remaining SCRs will see a higher current during fault and transition in one direction only. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 3 | Over Current. De-gradation of components. | Usage of over-rated components. | 1 | 3 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | On board SCR gate current measurement. | 3 | 9 | "In Bypass Telemetry field 'SCR and Clamp Board Status' will show following: SCR 1 (Output Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 2 (Mid 1 Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 3 (Mid 2 Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 4 (Input Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) | None. | Alert to be generated for the user to communicate the failure of one portion of SCR triggering path. | [8 empty] | -1402
SV104-5130 |  |  |  | Resistor fails-short. | Overcurrent will cause the resistor to fail-open. No power to on-board electronics for Gate current of single SCR. Loss of gate current for a single SCR. Remaining SCRs will see a higher current during fault and transition in one direction only. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 3 | Over Current. De-gradation of components. | Usage of over-rated components. | 1 | 3 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | On board SCR gate current measurement. | 3 | 9 | "In Bypass Telemetry field 'SCR and Clamp Board Status' will show following: SCR 1 (Output Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 2 (Mid 1 Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 3 (Mid 2 Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 4 (Input Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) | None. | Alert to be generated for the user to communicate the failure of one portion of SCR triggering path. | [8 empty] | -5130
SV104-1403 | 5 V Regulator Circuit - Current Limiting Resistor At Base Of Darlington Pair. | R15, R68, R161, R189, R198 | To limit current flow in the transistor. | Resistor fails-open. | No power to on-board electronics for Gate current of single SCR. Loss of gate current for a single SCR. Remaining SCRs will see a higher current during fault and transition in one direction only. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 3 | Over Current. De-gradation of components. | Usage of over-rated components. | 1 | 3 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | On board SCR gate current measurement. | 3 | 9 | "In Bypass Telemetry field 'SCR and Clamp Board Status' will show following: SCR 1 (Output Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 2 (Mid 1 Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 3 (Mid 2 Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 4 (Input Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) | None. | Alert to be generated for the user to communicate the failure of one portion of SCR triggering path. | [8 empty] | -1403
SV104-5131 |  |  |  | Resistor fails-short. | No immediate effect. There is not enough current to cause opening of this resistor. Transistor degradation could occur leading to its failure. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 2 | Over Current. De-gradation of components. | Usage of over-rated components. | 1 | 2 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | None. | 5 | 10 | None. | None. | Alert to be generated for the user to communicate the failure of one portion of SCR triggering path. | No immediate effect. There is not enough current to cause opening of this resistor. Transistor degradation could occur leading to its failure. PS19 Q&PI: Updated | [7 empty] | -5131
SV104-1404 | 5 V Regulator Circuit - Output Side Protection Diode. | D112, D115, D123, D126, D128 | To provide overvoltage protection. | Diode fails-open. | No immediate effect. Overvoltage protection for the circuit will be compromised. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 1 | Over Voltage De-gradation of components. | Usage of over-rated components. | 2 | 2 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | None. | 5 | 10 | None. | None. | Alert to be generated for the user to communicate the failure of one portion of SCR triggering path. | [8 empty] | -1404
SV104-5132 |  |  |  | Diode fails-short. | Overcurrent will cause the diode to eventually fail-open. No immediate effect. Overvoltage protection for the circuit will be compromised. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 1 | Over Voltage De-gradation of components. | Usage of over-rated components. | 1 | 1 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | None. | 5 | 5 | None. | None. | Alert to be generated for the user to communicate the failure of one portion of SCR triggering path. | [8 empty] | -5132
SV104-1405 | 5 V Regulator Circuit - Output Capacitor. | C33, C51, C85, C143, C162 | To provide smooth output. | Capacitor fails-open. | No immediate effect. Noise at output may cause on-board electronics to malfunction. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 1 | Over Voltage De-gradation of components. | Usage of over-rated components. | 1 | 1 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | None. | 5 | 5 | None. | None. | Alert to be generated for the user to communicate the failure of one portion of SCR triggering path. | [8 empty] | -1405
SV104-5133 |  |  |  | Capacitor fails-short. | Single SCR gate current circuit will be lost for the shorted duration. Remaining SCRs will see a higher current in mode transition and fault events. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 1 | Over Voltage De-gradation of components. | Usage of over-rated components. | 1 | 1 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. |  | 3 | 3 | "In Bypass Telemetry field 'SCR and Clamp Board Status' will show following: SCR 1 (Output Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 2 (Mid 1 Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 3 (Mid 2 Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 4 (Input Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) | None. | Alert to be generated for the user to communicate the failure of one portion of SCR triggering path. | Not enough current to cause opening the capacitor, so power supply to a single SCR gate current circuit will be lost. PS19 Q&PI: Updated | [7 empty] | -5133
SV104-1406 | 3.3 V Regulator Circuit - Input Side Filtration Capacitor. | C160, C169, C178, C187, C196 | To filter out noise. | Capacitor fails-open. | No immediate effect. Noise at output may cause on-board electronics to malfunction. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 1 | Over Voltage De-gradation of components. | Usage of over-rated components. | 1 | 1 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | None. | 5 | 5 | None. | None. | Alert to be generated for the user to communicate the failure of one portion of SCR triggering path. | [8 empty] | -1406
SV104-5134 |  |  |  | Capacitor fails-short. | Single SCR gate current circuit will be lost for the shorted duration. Remaining SCRs will see a higher current in mode transition and fault events. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 1 | Over Voltage De-gradation of components. | Usage of over-rated components. | 1 | 1 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. |  | 3 | 3 | "In Bypass Telemetry field 'SCR and Clamp Board Status' will show following: SCR 1 (Output Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 2 (Mid 1 Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 3 (Mid 2 Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 4 (Input Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) | None. | Alert to be generated for the user to communicate the failure of one portion of SCR triggering path. | Not enough current to cause opening the capacitor, so power supply to a single SCR gate current circuit will be lost. PS19 Q&PI: Updated | [7 empty] | -5134
SV104-1407 | 3.3 V Regulator Circuit - Output Side Filtration Capacitor. | C161, C170, C179, C188, C197 | To filter out noise. | Capacitor fails-open. | No immediate effect. Noise at output may cause on-board electronics to malfunction. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 1 | Over Voltage De-gradation of components. | Usage of over-rated components. | 1 | 1 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | None. | 5 | 5 | None. | None. | Alert to be generated for the user to communicate the failure of one portion of SCR triggering path. | [8 empty] | -1407
SV104-5135 |  |  |  | Capacitor fails-short. | No power to hall effect sensor. Continuous back porch not available to single SCR gate. SCR will turn on for first half-cycle only due to pulse current. SCR will be turned off for remaining half-cycles. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 1 | Over Voltage De-gradation of components. | Usage of over-rated components. | 1 | 1 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. |  | 3 | 3 | "In Bypass Telemetry field 'SCR and Clamp Board Status' will show following: SCR 1 (Output Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 2 (Mid 1 Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 3 (Mid 2 Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 4 (Input Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) | None. | Alert to be generated for the user to communicate the failure of one portion of SCR triggering path. | Not enough current to cause opening the capacitor, so No power to hall effect sensor. Continuous back porch not available to single SCR gate. SCR will turn on for first half-cycle only due to pulse current. SCR will be turned off for remaining half-cycles. Ps19 Q&PI: Updated | [7 empty] | -5135
SV104-1408 | 3.3 V Regulator Circuit - Regulator IC. | U51, U56, U61, U66, U71 | To provide regulated 3.3 V to Hall effect sensor. | IC failure . | No power to hall effect sensor. Continuous back porch not available to single SCR gate. SCR will turn on for first half-cycle only due to pulse current. SCR will be turned off for remaining half-cycles. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 3 | High voltage transients | 4 parallel SCRs in either direction to ensure loss of a single SCR will not endanger VSLs and other SCRs. | 2 | 6 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | On board SCR gate current measurement. | 3 | 18 | "In Bypass Telemetry field 'SCR and Clamp Board Status' will show following: SCR 1 (Output Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 2 (Mid 1 Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 3 (Mid 2 Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 4 (Input Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) | None. | [9 empty] | -1408
SV104-1409 | Constant Current Enable Circuit - 22 V Zener. | D82, D85, D88, D91, D94 | Over voltage protection. | Diode fails-open. | Continuous back porch not available to single SCR gate. SCR will be turned off. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 3 | High voltage transients | 4 parallel SCRs in either direction to ensure loss of a single SCR will not endanger VSLs and other SCRs. | 2 | 6 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | On board SCR gate current measurement. | 3 | 18 | "In Bypass Telemetry field 'SCR and Clamp Board Status' will show following: SCR 1 (Output Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 2 (Mid 1 Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 3 (Mid 2 Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 4 (Input Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) | None. | [9 empty] | -1409
SV104-5137 |  |  |  | Diode fails-short. | Overcurrent will cause the diode to eventually fail-open. Continuous back porch not available to single SCR gate. SCR will be turned off. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 3 | High voltage transients | 4 parallel SCRs in either direction to ensure loss of a single SCR will not endanger VSLs and other SCRs. | 2 | 6 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | On board SCR gate current measurement. | 3 | 18 | "In Bypass Telemetry field 'SCR and Clamp Board Status' will show following: SCR 1 (Output Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 2 (Mid 1 Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 3 (Mid 2 Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 4 (Input Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) | None. | [9 empty] | -5137
SV104-1410 | Constant Current Enable Circuit - Current Limit Resistor. | R290, R251, R302, R314, R326 | Limit the current through Zener. | Resistor fails-open | Continuous back porch not available to single SCR gate. SCR will be turned off. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 3 | High voltage transients | 4 parallel SCRs in either direction to ensure loss of a single SCR will not endanger VSLs and other SCRs. | 1 | 3 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | On board SCR gate current measurement. | 3 | 9 | "In Bypass Telemetry field 'SCR and Clamp Board Status' will show following: SCR 1 (Output Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 2 (Mid 1 Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 3 (Mid 2 Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 4 (Input Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) | None. | [9 empty] | -1410
SV104-5138 |  |  |  | Resistor fails-short. | Overcurrent will cause the resistor to eventually fail-open. Continuous back porch not available to single SCR gate. SCR will be turned off. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 3 | High voltage transients | 4 parallel SCRs in either direction to ensure loss of a single SCR will not endanger VSLs and other SCRs. | 1 | 3 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | On board SCR gate current measurement. | 3 | 9 | "In Bypass Telemetry field 'SCR and Clamp Board Status' will show following: SCR 1 (Output Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 2 (Mid 1 Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 3 (Mid 2 Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 4 (Input Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) | None. | [9 empty] | -5138
SV104-1411 | Constant Current Enable Circuit - Reverse Current Protection Diode. | D113, D129, D130, D131, D132 | Reverse Current Protection. | Diode fails-open. | Continuous back porch not available to single SCR gate. SCR will be turned off. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 3 | High voltage transients | 4 parallel SCRs in either direction to ensure loss of a single SCR will not endanger VSLs and other SCRs. | 2 | 6 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | On board SCR gate current measurement. | 3 | 18 | "In Bypass Telemetry field 'SCR and Clamp Board Status' will show following: SCR 1 (Output Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 2 (Mid 1 Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 3 (Mid 2 Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 4 (Input Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) | None. | [9 empty] | -1411
SV104-5139 |  |  |  | Diode fails-short. | Overcurrent will cause the diode to eventually fail-open. Continuous back porch not available to single SCR gate. SCR will be turned off. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 3 | High voltage transients | 4 parallel SCRs in either direction to ensure loss of a single SCR will not endanger VSLs and other SCRs. | 2 | 6 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | On board SCR gate current measurement. | 3 | 18 | "In Bypass Telemetry field 'SCR and Clamp Board Status' will show following: SCR 1 (Output Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 2 (Mid 1 Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 3 (Mid 2 Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 4 (Input Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) | None. | [9 empty] | -5139
SV104-1412 | Constant Current Enable Circuit - 5 V Regulator Check MOSFET. | Q66, Q67, Q68, Q69, Q70 | To check if 5 V regulator is working. | MOSFET fails-open. | No immediate effect. 5 V regulator check not available | Device can operate in both injection and monitoring mode. | System will keep working normally. | 1 | Over Voltage De-gradation of components. | Usage of over-rated components. | 1 | 1 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | None. | 5 | 5 | None. | None. | Alert to be generated for the user to communicate the failure of one portion of SCR triggering path. | [8 empty] | -1412
SV104-1413 |  |  |  | MOSFET fails-short | Continuous back porch not available to single SCR gate. SCR will be turned off. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 3 | High voltage transients | 4 parallel SCRs in either direction to ensure loss of a single SCR will not endanger VSLs and other SCRs. | 2 | 6 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | On board SCR gate current measurement. | 3 | 18 | "In Bypass Telemetry field 'SCR and Clamp Board Status' will show following: SCR 1 (Output Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 2 (Mid 1 Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 3 (Mid 2 Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 4 (Input Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) | None. | [9 empty] | -1413
SV104-1414 | Constant Current Enable Circuit - Trigger Transistor. | Q37, Q40, Q43, Q46, Q49 | Trigger timer IC to enable constant current circuit. | Transistor fails-short . | Continuous back porch not available to single SCR gate. SCR will be turned off. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 3 | High voltage transients | 4 parallel SCRs in either direction to ensure loss of a single SCR will not endanger VSLs and other SCRs. | 2 | 6 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. |  | 3 | 18 | "In Bypass Telemetry field 'SCR and Clamp Board Status' will show following: SCR 1 (Output Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 2 (Mid 1 Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 3 (Mid 2 Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 4 (Input Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) | None. | [9 empty] | -1414
SV104-1415 |  |  |  | Transistor fails-open. | Continuous back porch not available to single SCR gate. Single SCR may false triggered for 1.5 seconds in worst case. SCR will be turned off. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 3 | High voltage transients | 4 parallel SCRs in either direction to ensure loss of a single SCR will not endanger VSLs and other SCRs. | 2 | 6 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | None. | 5 | 30 | None. | None. | [9 empty] | -1415
SV104-1416 | Mono-pulse Enable Transistor. | Q36, Q39, Q42, Q45, Q48 | Trigger initial pulse enable circuit. | Transistor fails-open. | Initial pulse current will not be available to affected SCR gate but continuous back porch current will still be there. SCR may turn on due to continuous back porch. There is a probability that SCR may not turn on due to unavailability of initial pulse. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 3 | High voltage transients | 4 parallel SCRs in either direction to ensure loss of a single SCR will not endanger VSLs and other SCRs. | 2 | 6 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | None. | 5 | 30 | None. | None. | [9 empty] | -1416
SV104-5140 |  |  |  | Transistor fails-short. | Initial pulse current will not be available to affected SCR gate but continuous back porch current will still be there. SCR may turn on due to continuous back porch. There is a probability that SCR may not turn on due to unavailability of initial pulse. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 3 | High voltage transients | 4 parallel SCRs in either direction to ensure loss of a single SCR will not endanger VSLs and other SCRs. | 2 | 6 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | None. | 5 | 30 | None. | None. | [9 empty] | -5140
SV104-1417 | Constant Current Enable Circuit Timer IC. | U76, U81, U86, U96, U101 | Trigger constant current enable circuit for 1.43 seconds. | IC failure. (Permanent high). | Initial pulse and constant current enable circuits will not be functional. Device will be unable to initiate the trigger for single SCR in one direction when moving from injection mode to monitoring mode and vice versa.. | During mode transition, only 3 SCRs will be handling the line current in one direction. | System will keep working normally. | 3 | Over Current. De-gradation of components. | Usage of overrated components. | 2 | 6 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | On board SCR gate current measurement. | 3 | 18 | "In Bypass Telemetry field 'SCR and Clamp Board Status' will show following: SCR 1 (Output Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 2 (Mid 1 Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 3 (Mid 2 Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 4 (Input Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) | None. | Alert to be generated for the user to communicate the failure of one portion of SCR triggering path. | [8 empty] | -1417
SV104-1418 |  |  |  | IC failure. (Permanent low). | No immediate effect. SCRs may false trigger due to noise on SCR enable signal. In injection mode, False triggering will cause transition form injection to monitoring. | Device will switch to monitoring mode temporarily. Device will switch back to injection after 1.4 seconds. | Affected device and its associated group of devices will transit to monitoring mode temporarility. | 3 | Over Current. De-gradation of components. | Usage of overrated components. | 1 | 3 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | On board SCR gate current measurement. | 3 | 9 | "In Bypass Telemetry field 'SCR and Clamp Board Status' will show following: SCR 1 (Output Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 2 (Mid 1 Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 3 (Mid 2 Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 4 (Input Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) | None. | Alert to be generated for the user to communicate the failure of one portion of SCR triggering path. | false triggering will cause transition form from injection to monitoring PS19 Q&PI: Updated update higher level and other columns PS19 Q&PI: Updated | [7 empty] | -1418
SV104-1419 | Pulse Enable Circuit Timer IC. | U77, U82, U87, U97, U102 | Trigger initial pulse enable circuit. | IC failure. (Permanent high). | Pulse current circuit fails-short after providing an initial pulse. SCR is not triggered. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 3 | Over Current. De-gradation of components. | 4 parallel SCRs in either direction to ensure loss of a single SCR will not endanger VSLs and other SCRs. | 2 | 6 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. |  | 3 | 18 | "In Bypass Telemetry field 'SCR and Clamp Board Status' will show following: SCR 1 (Output Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 2 (Mid 1 Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 3 (Mid 2 Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 4 (Input Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) | None. | [9 empty] | -1419
SV104-1420 |  |  |  | IC failure. (Permanent low). | Initial pulse current will not be available to affected SCR gate but continuous back porch current will still be there. SCR may turn on due to continuous back porch. There is a probability that SCR may not turn on due to unavailability of initial pulse. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 3 | High voltage transients | 4 parallel SCRs in either direction to ensure loss of a single SCR will not endanger VSLs and other SCRs. | 2 | 6 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | None. | 5 | 30 | None. | None. | [9 empty] | -1420
SV104-1421 | Pulse Enable Circuit - Trigger Transistor. | Q38, Q41, Q44, Q47, Q50 | Trigger initial pulse enable circuit. | Transistor fails-short. | Initial pulse current will not be available to affected SCR gate but continuous back porch current will still be there. SCR may turn on due to continuous back porch. There is a probability that SCR may not turn on due to unavailability of initial pulse. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 3 | High voltage transients | 4 parallel SCRs in either direction to ensure loss of a single SCR will not endanger VSLs and other SCRs. | 2 | 6 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | None. | 5 | 30 | None. | None. | [9 empty] | -1421
SV104-1422 |  |  |  | Transistor fails-open | Pulse current circuit fails-short after providing an initial pulse. SCR is not triggered. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 3 | Over Current. De-gradation of components. | 4 parallel SCRs in either direction to ensure loss of a single SCR will not endanger VSLs and other SCRs. | 2 | 6 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. |  | 3 | 18 | "In Bypass Telemetry field 'SCR and Clamp Board Status' will show following: SCR 1 (Output Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 2 (Mid 1 Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 3 (Mid 2 Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 4 (Input Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) | None. | [9 empty] | -1422
SV104-1423 | Constant Current Enable Circuit - Logic Circuit - And Gate IC. | U48B, U79B, U94B, U99B, U104B | Enable constant current circuit to provide continuous back porch current. | IC Failure (Permanently High). | Gate current will start to flow continuously for the affected SCR. SCR will start conducting for every alternate half cycle. | SCR may fail-short due to over-temperature if this condition prevails for long duration. Device will stay in monitoring mode. | Affected device and its associated group of devices will transit to monitoring mode. System will keep working with reduced injection capability. | 4 | Over Current. De-gradation of components. | Usage of overrated components. | 2 | 8 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | On board SCR gate current measurement. | 3 | 24 | "In Bypass Telemetry field 'SCR and Clamp Board Status' will show following: SCR 1 (Output Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 2 (Mid 1 Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 3 (Mid 2 Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 4 (Input Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) | None. | Alert to be generated for the user to communicate the failure of one portion of SCR triggering path. | [8 empty] | -1423
SV104-1424 |  |  |  | IC Failure (Permanently Low). | Continuous back porch not available to single SCR gate. SCR will turn on for first half-cycle only due to pulse current. SCR will be turned off for remaining half-cycles. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 3 | Over Current. De-gradation of components. | 4 parallel SCRs in either direction to ensure loss of a single SCR will not endanger VSLs and other SCRs. | 2 | 6 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | On board SCR gate current measurement. | 3 | 18 | "In Bypass Telemetry field 'SCR and Clamp Board Status' will show following: SCR 1 (Output Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 2 (Mid 1 Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 3 (Mid 2 Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 4 (Input Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) | None. | [9 empty] | -1424
SV104-1425 | Pulse Current Enable Circuit - Logic Circuit - And Gate IC. | U48C, U79C, U94C, U99C, U104C | Enable initial pulse current circuit. | IC Failure (Permanently High). | Pulse current circuit fails-short after providing an initial pulse. SCR is not triggered. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 3 | Over Current. De-gradation of components. | 4 parallel SCRs in either direction to ensure loss of a single SCR will not endanger VSLs and other SCRs. | 2 | 6 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | On board SCR gate current measurement. | 3 | 18 | "In Bypass Telemetry field 'SCR and Clamp Board Status' will show following: SCR 1 (Output Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 2 (Mid 1 Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 3 (Mid 2 Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 4 (Input Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) | None. | Alert to be generated for the user to communicate the failure of one portion of SCR triggering path. | [8 empty] | -1425
SV104-1426 |  |  |  | IC Failure (Permanently Low). | Initial pulse current will not be available to affected SCR gate but continuous back porch current will still be there. SCR may turn on due to continuous back porch. There is a probability that SCR may not turn on due to unavailability of initial pulse. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 3 | Over Current. De-gradation of components. | 4 parallel SCRs in either direction to ensure loss of a single SCR will not endanger VSLs and other SCRs. | 2 | 6 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | On board SCR gate current measurement. | 3 | 18 | "In Bypass Telemetry field 'SCR and Clamp Board Status' will show following: SCR 1 (Output Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 2 (Mid 1 Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 3 (Mid 2 Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 4 (Input Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) | None. | Alert to be generated for the user to communicate the failure of one portion of SCR triggering path. | [8 empty] | -1426
SV104-13684 | SCR Enable Digital Isolator Circuit - Isolator IC | U49, U59, U62, U64, U67 | To provide isolation between SCR enable signal and constant current enable signal. | IC permanent failure. | SCR enable signal not available. SCR will turn on only due to pulse current. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 3 | Over Current. De-gradation of components. | 4 parallel SCRs in either direction to ensure loss of a single SCR will not endanger VSLs and other SCRs. | 2 | 6 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | On board SCR gate current measurement. | 3 | 18 | "In Bypass Telemetry field 'SCR and Clamp Board Status' will show following: SCR 1 (Output Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 2 (Mid 1 Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 3 (Mid 2 Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 4 (Input Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) | None. | [9 empty] | 13684
SV104-13685 | SCR Enable Digital Isolator Circuit - Anode/Cathode Resistor | R239, R270, R271, R272, R276, R277, R280, R281, R331, R332 | Limit current through isolator IC. | Resistor fails open. | Single SCR enable signal not available. SCR will turn on only due to pulse current. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 3 | Over Current. De-gradation of components. | 4 parallel SCRs in either direction to ensure loss of a single SCR will not endanger VSLs and other SCRs. | 1 | 3 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | On board SCR gate current measurement. | 3 | 9 | "In Bypass Telemetry field 'SCR and Clamp Board Status' will show following: SCR 1 (Output Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 2 (Mid 1 Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 3 (Mid 2 Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 4 (Input Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) | None. | [9 empty] | 13685
SV104-13686 |  |  |  | Resistor fails short. | No immediate effect. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 1 | Over Current. De-gradation of components. | Usage of overrated components. | 1 | 1 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | None. | 5 | 5 | None. | None. | [9 empty] | 13686
SV104-13687 | SCR Enable Digital Isolator Circuit - Voltage Divider Resistor | R265, R274, R275, R279, R330 | To provide voltage drop/reference to ground. | Resistor fails open. | No immediate effect. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 1 | Over Current. De-gradation of components. | Usage of overrated components. | 1 | 1 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | None. | 5 | 5 | None. | None. | [9 empty] | 13687
SV104-13688 |  |  |  | Resistor fails short. | Anode shorted to cathode. Single SCR enable signal not available. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 3 | Over Current. De-gradation of components. | 4 parallel SCRs in either direction to ensure loss of a single SCR will not endanger VSLs and other SCRs. | 1 | 3 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | On board SCR gate current measurement. | 3 | 9 | "In Bypass Telemetry field 'SCR and Clamp Board Status' will show following: SCR 1 (Output Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 2 (Mid 1 Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 3 (Mid 2 Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 4 (Input Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) | None. | [9 empty] | 13688
SV104-13689 | Single Inverter Gate IC. | U57, U60, U63, U65, U68, U78, U80, U83, U85, U88, U95, U98, U100, U103, U105 | To invert the enable signal. | Output stuck at low (IC failure). | Constant current enable signal not available. SCR may still turn on for sometime due to pulse current. Worst case scenario, SCR will not be triggered. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 3 | Over Current. De-gradation of components. | 4 parallel SCRs in either direction to ensure loss of a single SCR will not endanger VSLs and other SCRs. | 2 | 6 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | On board SCR gate current measurement. | 3 | 18 | "In Bypass Telemetry field 'SCR and Clamp Board Status' will show following: SCR 1 (Output Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 2 (Mid 1 Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 3 (Mid 2 Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 4 (Input Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) | None. | [9 empty] | 13689
SV104-13690 |  |  |  | Output stuck at high (IC failure). | Constant current signal may be stuck at high in worst case. | If device was in injection mode it will switch to monitoring mode. Device will remain in Monitoring mode as long as this issue persists. | Affected device and its associated group of devices will transit to monitoring mode. System will keep working with reduced injection capability. | 4 | Over Current. De-gradation of components. | Usage of overrated components. | 2 | 8 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | SCR current measurement from Rogowski coil. | 2 | 16 | In Bypass Telemetry field 'SCR and Clamp Board Status' will show following: SCR 1 (Output Side): SCRs On OR SCR 2 (Mid 1 Side): SCRs On OR SCR 3 (Mid 2 Side): SCRs On OR SCR 4 (Input Side): SCRs On | On SmartInterface following Alarm will be raised: If SCR > 100 SCR Failed Short If Line Current > 80A && SCR firing duration = 10 mins SCR Prolong Firing | [9 empty] | 13690
SV104-13691 | Voltage Supply Filtering Capacitor | C194, C195, C202, C203, C240, C241, C242, C243, C248, C263, C259, C168, C213, C833, C221, C215, C214, C136, C260, C186, C145, C189, C211, C205, C206, C146, C175, C173, C261, C190, C191, C230, C224, C225, C223, C177, C180, C262, C192, C193, C239, C233, C234, C232, C199, C200 | To filter supply voltage noise. | Capacitor fails-open. | No immediate effect. Noise at output may cause on-board electronics to malfunction. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 1 | Over Voltage De-gradation of components. | Usage of over-rated components. | 1 | 1 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | None. | 5 | 5 | None. | None. | [9 empty] | 13691
SV104-13692 |  |  |  | Capacitor fails-short. | No immediate effect. The respective active device will get stuck at low or high output. Cascading shortage of supply voltage capacitors may cause reduction of single SCR gate current. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 1 | Over Voltage De-gradation of components. | Usage of over-rated components. | 1 | 1 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | None. | 5 | 5 | None. | None. | [9 empty] | 13692
SV104-1427 | SCR Pulse And Constant Current Enable Circuit - Optical Isolator. | U46, U72, U89, U112, U119 | Isolate the enable signal. | Out stuck at high. | Continuous back porch and initial pulse current not available to single SCR gate. SCR will not be triggered. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 3 | Over Current. De-gradation of components. | 4 parallel SCRs in either direction to ensure loss of a single SCR will not endanger VSLs and other SCRs. | 2 | 6 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | On board SCR gate current measurement. | 3 | 18 | "In Bypass Telemetry field 'SCR and Clamp Board Status' will show following: SCR 1 (Output Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 2 (Mid 1 Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 3 (Mid 2 Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 4 (Input Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) | None. | Alert to be generated for the user to communicate the failure of one portion of SCR triggering path. | [8 empty] | -1427
SV104-1428 |  |  |  | Output stuck at low. | No immediate effect. SCRs may false trigger for 1.5s in worst case due to noise on timer IC enable signal. In injection mode. False triggering will cause transition form from injection to monitoring. | Device will switch to monitoring mode temporarily. Device will switch back to injection after 1.4 seconds. | Affected device and its associated group of devices will transit to monitoring mode temporarility. | 3 | Over Current. De-gradation of components. | Usage of overrated components. | 1 | 3 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | None. | 5 | 15 | None. | None. | Alert to be generated for the user to communicate the failure of one portion of SCR triggering path. | false triggering will cause transition form from injection to monitoring PS19 Q&PI: Updated update higher level and other columns PS19 Q&PI: Updated | [7 empty] | -1428
| SCR Gate Driver Board - Surge Detector | [26 empty] | 0
SV104-1430 | Line Current Sensing Connector. | CON6 | To sense fault current. | Cable break. | On-board fault detection will not be available. Reduced redundancy in case of fault events | Device can operate in both injection and monitoring mode. | System will keep working normally. | 3 | Vibration. Improper bend radius during assembly. | Connectors with secure contact mating. | 1 | 3 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | None. | 5 | 15 | None. | None. | [7 empty] | 0 | Approved | -1430
SV104-1431 | Input Side Filtering Capacitors. | C311, C307 | To filter out noise. | Capacitor fails-open. | Noise may cause a maximum of 1.5 seconds false trigger of SCRs In case of false trigger, device will temporarily switch to Monitoring mode. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 3 | Over Current. De-gradation of components. | Usage of over-rated components. | 1 | 3 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | None. | 5 | 15 | None. | None. | [9 empty] | -1431
SV104-5141 |  |  |  | Capacitor fails-short. | On-board fault detection will not be available. Reduced redundancy in case of fault events | Device can operate in both injection and monitoring mode. | System will keep working normally. | 3 | Vibration. Improper bend radius during assembly. | Usage of over-rated components. | 1 | 3 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | None. | 5 | 15 | None. | None. |  | PS19 Q&PI: This was highlighted but no comment is mentioned. Kindly confirm if this entry is okay. NOT ENOUGH CURRENT TO CAUSE OPENING, short will cause loss of line current detection PS19 Q&PI: Updated | [7 empty] | -5141
SV104-1432 | TVS Diode. | D99, D101, D103 | Transient Protection. | Diode fails-open. | Noise may cause a maximum of 1.5 seconds false trigger of SCRs In case of false trigger, device will temporarily switch to Monitoring mode. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 3 | Over Current. De-gradation of components. | Usage of over-rated components. | 2 | 6 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | None. | 5 | 30 | None. | None. | [9 empty] | -1432
SV104-5142 |  |  |  | Diode fails-short. | On-board fault detection will not be available. Reduced redundancy in case of fault events | Device can operate in both injection and monitoring mode. | System will keep working normally. | 3 | Vibration. Improper bend radius during assembly. | Usage of over-rated components. | 1 | 3 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | None. | 5 | 15 | None. | None. |  | PS19 Q&PI: This was highlighted but no comment is mentioned. Kindly confirm if this entry is okay. NOT ENOUGH CURRENT TO CAUSE OPENING, short will cause loss of line current detection PS19 Q&PI: Updated | [7 empty] | -5142
SV104-1433 | Common Mode Choke. | L19 | Noise Suppression. | CMC fails-open. | On-board fault detection will not be available. Reduced redundancy in case of fault events | Device can operate in both injection and monitoring mode. | System will keep working normally. | 3 | Vibration. Improper bend radius during assembly. | Usage of over-rated components. | 1 | 3 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | None. | 5 | 15 | None. | None. | [9 empty] | -1433
SV104-5143 |  |  |  | CMC fails-short. | On-board fault detection will not be available. Reduced redundancy in case of fault events | Device can operate in both injection and monitoring mode. | System will keep working normally. | 3 | Vibration. Improper bend radius during assembly. | Usage of over-rated components. | 1 | 3 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | None. | 5 | 15 | None. | None. | [9 empty] | -5143
SV104-9789 | Gain Amplifier | U133A | To amplify the signal. | IC Failure. (Permanent Low) | On-board fault detection will not be available. Reduced redundancy in case of fault events | Device can operate in both injection and monitoring mode. | System will keep working normally. | 3 | Vibration. Improper bend radius during assembly. | Usage of over-rated components. | 2 | 6 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | None. | 5 | 30 | None. | None. |  | Include failure cases for 4.3 gain Amplifier PS19 Q&PI: Updated | [7 empty] | -9789
SV104-9790 |  |  |  | IC Failure. (Permanent High) | All SCRs will be continuously triggered. Device cannot enter into injection mode. At line current above 9-15 kA Pk, the affected SCRs will start conducting. | If device was in injection mode it will switch to monitoring mode. Device will remain in Monitoring mode as long as this issue persists. | Affected device and its associated group of devices will transit to monitoring mode. System will keep working with reduced injection capability. | 4 | Over Current. De-gradation of components. | Usage of over-rated components. | 2 | 8 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | SCR current measurement from Rogowski coil. | 2 | 16 | In Bypass Telemetry field 'SCR and Clamp Board Status' will show following: SCR 1 (Output Side): SCRs On OR SCR 2 (Mid 1 Side): SCRs On OR SCR 3 (Mid 2 Side): SCRs On OR SCR 4 (Input Side): SCRs On | On SmartInterface following Alarm will be raised: If SCR > 100 SCR Failed Short If Line Current > 80A && SCR firing duration = 10 mins SCR Prolong Firing | [9 empty] | -9790
SV104-13693 | Gain Amplifier - Feedback Resistors | R438, R459 | To increase gain of the op-amp. | Resistor fails short. | Gain will be affected. Surge detection will be affected. Worst case scenario, on board fault detection will not be available. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 3 | Over Current. De-gradation of components. | Usage of over-rated components. | 1 | 3 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | None. | 5 | 15 | None. | None. | [9 empty] | 13693
SV104-13694 |  |  |  | Resistor fails open. | Gain will be affected. Surge detection will be affected. Worst case scenario, on board fault detection will not be available. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 3 | Over Current. De-gradation of components. | Usage of over-rated components. | 1 | 3 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | None. | 5 | 15 | None. | None. | [9 empty] | 13694
SV104-13695 | Gain Amplifier - Non-Inverting RC Circuit | C309, C314, C315, C316, R439, R448 | To provide reference voltage for op-amp gain. | Resistor/Capacitor fails short. | Surge current sensing will not be available. On-board fault detection will not be available. Reduced redundancy in case of fault events | Device can operate in both injection and monitoring mode. | System will keep working normally. | 3 | Over Current. De-gradation of components. | Usage of over-rated components. | 1 | 3 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | None. | 5 | 15 | None. | None. | [9 empty] | 13695
SV104-13696 |  |  |  | Resistor/Capacitor fails open. | No immediate effect. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 1 | Over Current. De-gradation of components. | Usage of over-rated components. | 1 | 1 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | None. | 5 | 5 | None. | None. | [9 empty] | 13696
SV104-1434 | Signal Conditioning Components For Gain Amplifier - Series Resistor. | R441 | Input compensating resistor. | Resistor fails-open. | On-board fault detection will not be available. Reduced redundancy in case of fault events | Device can operate in both injection and monitoring mode. | System will keep working normally. | 3 | Vibration. Improper bend radius during assembly. | Usage of over-rated components. | 1 | 3 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | None. | 5 | 15 | None. | None. | [9 empty] | -1434
SV104-5144 |  |  |  | Resistor fails-short. | On-board fault detection will not be available. Reduced redundancy in case of fault events | Device can operate in both injection and monitoring mode. | System will keep working normally. | 3 | Vibration. Improper bend radius during assembly. | Usage of over-rated components. | 1 | 3 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | None. | 5 | 15 | None. | None. | [9 empty] | -5144
SV104-1435 | Integrator Circuit - Amplifier. | U134A | To provide phase shift. | IC failure. | On-board fault detection will not be available. Reduced redundancy in case of fault events | Device can operate in both injection and monitoring mode. | System will keep working normally. | 3 | Vibration. Improper bend radius during assembly. | Usage of over-rated components. | 2 | 6 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | None. | 5 | 30 | None. | None. | [9 empty] | -1435
SV104-1436 | Integrator Circuit - Gain Resistor. | R440 | To set gain of amplifier. | Resistor fails-open. | Phase shift will be affected. Gain will be affected. On-board line current sensing will be affected. False overcurrent/surge events may be triggered. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 3 | Degradation of components. Bad components batch. | Usage of over-rated components. | 1 | 3 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | On board SCR gate current measurement. | 4 | 12 | "In Bypass Telemetry field 'SCR and Clamp Board Status' will show following: SCR 1 (Output Side): SCRs On OR SCR 2 (Mid 1 Side): SCRs On OR SCR 3 (Mid 2 Side): TSCRs On OR SCR 4 (Input Side): SCRs On | None. | [9 empty] | -1436
SV104-5145 |  |  |  | Resistor fails-short. | Overcurrent will cause the resistor to eventually fail-open. Phase shift will be affected. Gain will be affected. On-board line current sensing will be affected. False overcurrent/surge events may be triggered. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 3 | Degradation of components. Bad components batch. | Usage of over-rated components. | 1 | 3 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | On board SCR gate current measurement. | 4 | 12 | "In Bypass Telemetry field 'SCR and Clamp Board Status' will show following: SCR 1 (Output Side): SCRs On OR SCR 2 (Mid 1 Side): SCRs On OR SCR 3 (Mid 2 Side): TSCRs On OR SCR 4 (Input Side): SCRs On | None. | [9 empty] | -5145
SV104-1437 | Integrator Circuit - Gain Capacitor. | C130 | To set gain of amplifier. | Capacitor fails-open. | Phase shift will be affected. Gain will be affected. On-board line current sensing will be affected. False overcurrent/surge events may be triggered. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 3 | Degradation of components. Bad components batch. | Usage of over-rated components. | 1 | 3 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | On board SCR gate current measurement. | 4 | 12 | "In Bypass Telemetry field 'SCR and Clamp Board Status' will show following: SCR 1 (Output Side): SCRs On OR SCR 2 (Mid 1 Side): SCRs On OR SCR 3 (Mid 2 Side): TSCRs On OR SCR 4 (Input Side): SCRs On | None. | [9 empty] | -1437
SV104-1438 | Surge Comparator For Positive-Cycle. | U135 | To compare surge signal and reference voltages for positive-cycle. | IC failure - Permanent high signal at output. | Hardware-based protection will be affected for positive cycle. On-board line current sensing will be affected. | Device will keep working normally based on firmware-based protection. | System will keep working normally. | 3 | Degradation of components. Bad batch of components. | Redundant surge sensors. In case of injection SV current sensor will trigger fault protection. Dedicated surge detection sensor on SVMC board will be used for fault protection. | 2 | 6 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | None. | 5 | 30 | None. | None. | [9 empty] | -1438
SV104-1439 |  |  |  | IC failure - Permanent low signal at output. | All SCRs will be continuously triggered. Device cannot enter into injection mode. At line current above 9-15 kA Pk, the affected SCRs will start conducting. | If device was in injection mode it will switch to monitoring mode. Device will remain in Monitoring mode as long as this issue persists. | Affected device and its associated group of devices will transit to monitoring mode. System will keep working with reduced injection capability. | 4 | Over Current. De-gradation of components. | Usage of over-rated components. | 2 | 8 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | SCR current measurement from Rogowski coil. | 2 | 16 | In Bypass Telemetry field 'SCR and Clamp Board Status' will show following: SCR 1 (Output Side): SCRs On OR SCR 2 (Mid 1 Side): SCRs On OR SCR 3 (Mid 2 Side): SCRs On OR SCR 4 (Input Side): SCRs On | On SmartInterface following Alarm will be raised: If SCR > 100 SCR Failed Short If Line Current > 80A && SCR firing duration = 10 mins SCR Prolong Firing |  | All SCRs will be continuously triggered. System will transit from injection to monitoring mode PS19 Q&PI: Updated | [7 empty] | -1439
SV104-1440 | Surge Comparator-For Negative Half Cycle. | U140 | To compare surge signal and reference voltages for negative-cycle. | IC failure - Permanent high signal at output. | Hardware-based protection will be affected for negative cycle. On-board line current sensing will be affected. | Device will keep working normally based on firmware-based protection. | System will keep working normally. | 3 | Degradation of components. Bad batch of components. | Redundant surge sensors. In case of injection SV current sensor will trigger fault protection. Dedicated surge detection sensor on SVMC board will be used for fault protection. | 2 | 6 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | None. | 5 | 30 | None. | None. | [9 empty] | -1440
SV104-1441 |  |  |  | IC failure - Permanent low signal at output. | All SCRs will be continuously triggered. Device cannot enter into injection mode. At line current above 9-15 kA Pk, the affected SCRs will start conducting. | If device was in injection mode it will switch to monitoring mode. Device will remain in Monitoring mode as long as this issue persists. | Affected device and its associated group of devices will transit to monitoring mode. System will keep working with reduced injection capability. | 4 | Over Current. De-gradation of components. | Usage of over-rated components. | 2 | 8 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | SCR current measurement from Rogowski coil. | 2 | 16 | In Bypass Telemetry field 'SCR and Clamp Board Status' will show following: SCR 1 (Output Side): SCRs On OR SCR 2 (Mid 1 Side): SCRs On OR SCR 3 (Mid 2 Side): SCRs On OR SCR 4 (Input Side): SCRs On | On SmartInterface following Alarm will be raised: If SCR > 100 SCR Failed Short If Line Current > 80A && SCR firing duration = 10 mins SCR Prolong Firing |  | All SCRs will be continuously triggered. System will transit from injection to monitoring mode PS19 Q&PI: Updated | [7 empty] | -1441
SV104-1442 | Surge-Comparator Output Pull-Up Resistor. | R455 | To pull-up the output of surge comparator. | Resistor fails-open. | Output of comparator will be floating. On-board line current sensing will be affected. | False overcurrent/surge events may be triggered. Device may be unable to detect overcurrent/surge scenarios using line current sensing capability. Dedicated surge detection sensor on SVMC board will be used for fault protection. | System will keep working normally. | 3 | Degradation of components. Bad batch of components. | Usage of over-rated resistors. Redundant surge sensors. In case of injection SV current sensor will trigger fault protection. Dedicated surge detection sensor on SVMC board will be used for fault protection. | 1 | 3 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | None. | 5 | 15 | None. | None. | [9 empty] | -1442
SV104-5146 |  |  |  | Resistor fails-short. | Overcurrent will cause the resistor to eventually fail-open. Output of comparator will be floating. On-board line current sensing will be affected. | False overcurrent/surge events may be triggered. Device may be unable to detect overcurrent/surge scenarios using line current sensing capability. Dedicated surge detection sensor on SVMC board will be used for fault protection. | System will keep working normally. | 3 | Degradation of components. Bad batch of components. | Usage of over-rated resistors. Redundant surge sensors. In case of injection SV current sensor will trigger fault protection. Dedicated surge detection sensor on SVMC board will be used for fault protection. | 1 | 3 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | None. | 5 | 15 | None. | None. | [9 empty] | -5146
SV104-1443 | Surge-Comparator Feedback Resistor. | R453, R460 | To provide feedback of comparator output. | Resistor fails-open. | Loss of hysteresis in comparator. On-board line current sensing will be affected. | Device will keep working normally based on firmware-based protection. | System will keep working normally. | 3 | Degradation of components. Bad batch of components. | Usage of over-rated resistors. Dedicated surge detection sensor on SVMC board will be used for fault protection. | 1 | 3 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | None. | 5 | 15 | None. | None. |  | There is a feedback resistor; not output resistor. Opening will cause loss of hysteresis in comparator PS19 Q&PI: Updated | [7 empty] | -1443
SV104-5147 |  |  |  | Resistor fails-short. | Hardware-based fault detection will be reduced. On-board line current sensing will be affected. | Device will keep working normally based on firmware-based protection. | System will keep working normally. | 3 | Degradation of components. Bad batch of components. | Usage of over-rated resistors. Dedicated surge detection sensor on SVMC board will be used for fault protection. | 1 | 3 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | None. | 5 | 15 | None. | None. |  | There is a feedback resistor; not output resistor. Shorting will effect the redundant surge detection in one direction PS19 Q&PI: Updated | [7 empty] | -5147
SV104-1444 | Comparator Circuit - 2.5 V Reference. | U142 | To provide positive / negative reference voltage to comparator. | IC failure. | On-board line current sensing will be affected. False overcurrent/surge events may be triggered. Device will leave injection mode as long as false surge events is detected. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 3 | Degradation of components. Bad components batch. | Usage of over-rated components. | 2 | 6 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | On board SCR gate current measurement. | 4 | 24 | "In Bypass Telemetry field 'SCR and Clamp Board Status' will show following: SCR 1 (Output Side): SCRs On OR SCR 2 (Mid 1 Side): SCRs On OR SCR 3 (Mid 2 Side): TSCRs On OR SCR 4 (Input Side): SCRs On | None. | [9 empty] | -1444
SV104-13697 | Comparator Circuit - 2.5V Input Capacitors | C334, C335 | To filter input voltages noise. | Both Capacitors fail open. | No immediate effect. Noise may cause ripples in 2.5 V output. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 1 | Degradation of components. Bad components batch. | Usage of over-rated components. | 1 | 1 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | None. | 5 | 5 | None. | None. | [9 empty] | 13697
SV104-13698 |  |  |  | Capacitor fails short. | Input shorted with ground. 2.5V supply not available to the board. False overcurrent/surge events may be triggered. Device will leave injection mode as long as false surge events is detected. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 3 | Degradation of components. Bad components batch. | Usage of over-rated components. | 1 | 3 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | On board SCR gate current measurement. | 4 | 12 | "In Bypass Telemetry field 'SCR and Clamp Board Status' will show following: SCR 1 (Output Side): SCRs On OR SCR 2 (Mid 1 Side): SCRs On OR SCR 3 (Mid 2 Side): SCRs On OR SCR 4 (Input Side): SCRs On | None. | [9 empty] | 13698
SV104-13699 | Comparator Circuit - 2.5V Output Capacitors | C338, C339, C340 | To filter output voltages noise. | Both Capacitors fail open. | No immediate effect. Noise may cause ripples in 2.5 V output. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 1 | Degradation of components. Bad components batch. | Usage of over-rated components. | 1 | 1 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | None. | 5 | 5 | None. | None. | [9 empty] | 13699
SV104-13700 |  |  |  | Capacitor fails short. | Input shorted with ground. 2.5V supply not available to the board. False overcurrent/surge events may be triggered. Device will leave injection mode as long as false surge events is detected. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 3 | Degradation of components. Bad components batch. | Usage of over-rated components. | 1 | 3 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | On board SCR gate current measurement. | 4 | 12 | "In Bypass Telemetry field 'SCR and Clamp Board Status' will show following: SCR 1 (Output Side): SCRs On OR SCR 2 (Mid 1 Side): SCRs On OR SCR 3 (Mid 2 Side): SCRs On OR SCR 4 (Input Side): SCRs On | None. | [9 empty] | 13700
SV104-1445 | Comparator Circuit - Positive Supply Buffer Amplifier. | U141A | To provide positive reference voltage to comparator. | IC failure. | Onboard line current sensing in one cycle will be affected. Reduced redundancy in case of fault events. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 3 | Over Current. De-gradation of components. | Usage of over-rated components. | 2 | 6 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | None. | 5 | 30 | None. | None. | [9 empty] | -1445
SV104-1446 | Comparator Circuit - Negative Supply Buffer Amplifier. | U141B | To provide negative reference voltage to comparator. | IC failure. | Onboard line current sensing in one cycle will be affected. Reduced redundancy in case of fault events. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 3 | Over Current. De-gradation of components. | Usage of over-rated components. | 2 | 6 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | None. | 5 | 30 | None. | None. | [9 empty] | -1446
SV104-13701 | Voltage Supply Filtering Capacitor | C312, C313, C317, C319, C321, C324, C327, C328, C329, C336, C333, C337 C352, C355, | To filter supply voltage noise. | Capacitor fails-open. | No immediate effect. Noise at output may cause on-board electronics to malfunction. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 1 | Over Voltage De-gradation of components. | Usage of over-rated components. | 1 | 1 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | None. | 5 | 5 | None. | None. | [9 empty] | 13701
SV104-13702 |  |  |  | Capacitor fails-short. | No immediate effect. The respective active device will get stuck at low or high output. Cascading shortage of supply voltage capacitors may cause reduction of single SCR gate current. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 1 | Over Voltage De-gradation of components. | Usage of over-rated components. | 1 | 1 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | None. | 5 | 5 | None. | None. | [9 empty] | 13702
SV104-1447 | Monoshot Vibrator. | U136A | Trigger SCRs for 1.5 seconds in case of on-board surge detection. | IC failure. (Permanent low). | All SCRs will be continuously triggered. Device cannot enter into injection mode. At line current above 9-15 kA Pk, the affected SCRs will start conducting. | If device was in injection mode it will switch to monitoring mode. Device will remain in Monitoring mode as long as this issue persists. | Affected device and its associated group of devices will transit to monitoring mode. System will keep working with reduced injection capability. | 4 | Over Current. De-gradation of components. | Usage of over-rated components. | 2 | 8 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | SCR current measurement from Rogowski coil. | 2 | 16 | In Bypass Telemetry field 'SCR and Clamp Board Status' will show following: SCR 1 (Output Side): SCRs On OR SCR 2 (Mid 1 Side): SCRs On OR SCR 3 (Mid 2 Side): SCRs On OR SCR 4 (Input Side): SCRs On | On SmartInterface following Alarm will be raised: If SCR > 100 SCR Failed Short If Line Current > 80A && SCR firing duration = 10 mins SCR Prolong Firing | [9 empty] | -1447
SV104-1448 |  |  |  | IC failure. (permanent high). | Onboard line current sensing in one cycle will be affected. Reduced redundancy in case of fault events. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 3 | Over Current. De-gradation of components. | Usage of over-rated components. | 2 | 6 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | None. | 5 | 30 | None. | None. | [9 empty] | -1448
SV104-13703 | Monoshot Vibrator - External RC Circuit | R456, C323 | To control output pulse duration. | Resistor/Capacitor fails open. | Output pulse not available. Onboard line current sensing in one cycle will be affected. Reduced redundancy in case of fault events. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 3 | Over Current. De-gradation of components. | Usage of over-rated components. | 1 | 3 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | None. | 5 | 15 | None. | None. | [9 empty] | 13703
SV104-1449 | Inverter IC. | U137 | To implement hardware logic of signals. | Output stuck at permanent high. | All SCRs will be continuously triggered. Device cannot enter into injection mode. At line current above 9-15 kA Pk, the affected SCRs will start conducting. | If device was in injection mode it will switch to monitoring mode. Device will remain in Monitoring mode as long as this issue persists. | Affected device and its associated group of devices will transit to monitoring mode. System will keep working with reduced injection capability. | 4 | Over Current. De-gradation of components. | Usage of over-rated components. | 2 | 8 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | SCR current measurement from Rogowski coil. | 2 | 16 | In Bypass Telemetry field 'SCR and Clamp Board Status' will show following: SCR 1 (Output Side): SCRs On OR SCR 2 (Mid 1 Side): SCRs On OR SCR 3 (Mid 2 Side): SCRs On OR SCR 4 (Input Side): SCRs On | On SmartInterface following Alarm will be raised: If SCR > 100 SCR Failed Short If Line Current > 80A && SCR firing duration = 10 mins SCR Prolong Firing | [9 empty] | -1449
SV104-13704 | Optical Transmitter | U138, U143, U144 | Provide optical feedback signal to SVMC board. | Output stuck at permanent high. | On board Surge detection signal will continuously trigger SCRs. Device will not be able to switch to Injection mode. | Device's default behavior will be to disallow injection mode operation. The device is capable of injection, however, and end user may request to override this protection. | Affected device and its associated group of devices will transit to monitoring mode. System will keep working with reduced injection capability. | 4 | Degradation of components. Bad components batch. | Usage of over-rated components. | 2 | 8 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | SCR current measurement from Rogowski coil. | 2 | 16 | In Bypass Telemetry field 'SCR and Clamp Board Status' will show following: SCR 1 (Output Side): SCRs On OR SCR 2 (Mid 1 Side): SCRs On OR SCR 3 (Mid 2 Side): SCRs On OR SCR 4 (Input Side): SCRs On | On SmartInterface following Alarm will be raised: If SCR > 100 SCR Failed Short If Line Current > 80A && SCR firing duration = 10 mins SCR Prolong Firing | [9 empty] | 13704
SV104-13705 |  |  |  | Output stuck at permanent low. | On board Surge detection not available to fire SCRs due to Surge Detection. SVMC board will still be able to trigger SCRs in case of Surge Detection. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 3 | Degradation of components. Bad components batch. | Usage of over-rated components. | 2 | 6 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | None. | 5 | 30 | None. | None. | [9 empty] | 13705
SV104-13706 | Optical Transmitter - Ground Capacitors | C325, C326, C353, C354, C356, C357 | To filter inductor ripples. | Capacitor fails short. | 5V Supply gets shorted to ground. On board SCR gate current feedback not available to SVMC board. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 1 | Over Voltage De-gradation of components. | Usage of over-rated components. | 1 | 1 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | None. | 5 | 5 | None. | None. | [9 empty] | 13706
SV104-13707 |  |  |  | Capacitor fails open. | No immediate effect. There maybe a floating point voltage that can cause a false signal. On board SCR gate current feedback to SVMC board might be compromised. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 1 | Over Voltage De-gradation of components. | Usage of over-rated components. | 1 | 1 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | None. | 5 | 5 | None. | None. | [9 empty] | 13707
SV104-13708 | Optical Transmitter - Data In Pull-down Resistor | R491, R492, R458 | To provide referenced voltages for optical signal. | Resistor fails short. | No input voltages available at the pin. Transmitter will not be able to send any signal. On board SCR gate current feedback not available to SVMC board. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 1 | Over Voltage De-gradation of components. | Usage of over-rated components. | 1 | 1 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | None. | 5 | 5 | None. | None. | [9 empty] | 13708
SV104-13709 |  |  |  | Resistor fails open. | No immediate effect. There maybe a floating point voltage that can cause a false signal. On board SCR gate current feedback to SVMC board might be compromised. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 1 | Over Voltage De-gradation of components. | Usage of over-rated components. | 1 | 1 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | None. | 5 | 5 | None. | None. | [9 empty] | 13709
SV104-1450 | Optical Transmitter - Application Circuit - Inductor. | L20, L22, L23 | Suppress supply voltage noise. | Inductor fails-open. | Onboard line current sensing in one cycle will be affected. Reduced redundancy in case of fault events. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 3 | Over Current. De-gradation of components. | Usage of over-rated components. | 1 | 3 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | None. | 5 | 15 | None. | None. | [9 empty] | -1450
SV104-5148 |  |  |  | Inductor fails-short. | Overcurrent will cause the inductor to eventually fail-open. Onboard line current sensing in one cycle will be affected. Reduced redundancy in case of fault events. | Device can operate in both injection and monitoring mode. | System will keep working normally. |  | Over Current. De-gradation of components. | Usage of over-rated components. |  | 0 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | On board SCR gate current measurement. |  | 0 |  |  |  | this case is not worth considering PS19 Q&PI: Updated | [7 empty] | -5148
| SCR Gate Driver Board - Synchronizer | [26 empty] | 0
SV104-1452 | 30 V Rail Power Good Circuit - 22 V Zener. | D140, D149 | Overvoltage protection. | Diodes in one of the rails fail-open | No immediate effect. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 1 | Over Current. De-gradation of components. | Usage of over-rated components. | 2 | 2 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | None. | 5 | 10 | None. | None. | [7 empty] | 0 | Approved | -1452
SV104-1453 |  |  |  | Diodes on both rails fail-open. | 30 V rail power good signal not available. Initial pulse and constant current enable circuits will not be functional. Fault-current handling not available in one direction. Device will be unable to initiate the trigger for all SCRs in one direction when moving from injection mode to monitoring mode and vice versa. | During mode transition, no SCR will be handling the line current in one direction. VSLs and device internals may get damaged in case of surge current event. | System will keep working normally. | 3 | Over Current. De-gradation of components. | Usage of over-rated components. | 1 | 3 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | On board SCR gate current measurement. | 2 | 6 | In Bypass Telemetry field 'SCR and Clamp Board Status' will show following: SCR 1 (Output Side): SCRs Off OR SCR 2 (Mid 1 Side): SCRs Off OR SCR 3 (Mid 2 Side): SCRs Off OR SCR 4 (Input Side): SCRs Off | On SmartInterface following Alarm will be raised: If SCR < 100 Permanent Injection Lockout | [9 empty] | -1453
SV104-1454 | 30 V Rail Power Good Circuit - Decoupling Capacitor. | C105, C270 | To suppress noise. | Capacitor fails-open. | No immediate effect. Reduced filtration. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 1 | Over Current. De-gradation of components. | Usage of over-rated components. | 1 | 1 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | None. | 5 | 5 | None. | [10 empty] | -1454
SV104-13710 | 30 V Rail Power Good Circuit - Voltage Divider Resistors | R173, R176, R375, R388 | To provide operating voltages for transistors. | Resistor fails open. | No immediate effect. Other circuit will provide the power good feedback. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 1 | Over Current. De-gradation of components. | Usage of over-rated components. | 1 | 1 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | None. | 5 | 5 | None. | None. | [9 empty] | 13710
SV104-13711 |  |  |  | Both Resistor fails open. | Power good feedback not available to the circuit. Initial pulse and constant current enable circuits will not be functional. Fault-current handling not available in one direction. Device will be unable to initiate the trigger for all SCRs in one direction when moving from injection mode to monitoring mode and vice versa. | During mode transition, no SCR will be handling the line current in one direction. VSLs and device internals may get damaged in case of surge current event. | System will keep working normally. | 3 | Over Current. De-gradation of components. | Usage of over-rated components. | 1 | 3 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | On board SCR gate current measurement. | 2 | 6 | In Bypass Telemetry field 'SCR and Clamp Board Status' will show following: SCR 1 (Output Side): SCRs Off OR SCR 2 (Mid 1 Side): SCRs Off OR SCR 3 (Mid 2 Side): SCRs Off OR SCR 4 (Input Side): SCRs Off | On SmartInterface following Alarm will be raised: If SCR < 100 Permanent Injection Lockout | [9 empty] | 13711
SV104-13712 | 30 V Rail Power Good Circuit - Current Limiting Resistor | R228, R394 | Limiting current through the circuit. | Resistor fails open. | No immediate effect. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 1 | Over Current. De-gradation of components. | Usage of over-rated components. | 1 | 1 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | None. | 5 | 5 | None. | None. | [9 empty] | 13712
SV104-13713 |  |  |  | Resistor fails short. | Increased current through circuit and transistor base to emitter voltage drops to zero. One half of power good rail check is lost. Worst case scenario, both power good rail checks are not available. Initial pulse and constant current enable circuits will not be functional. Fault-current handling not available in one direction. Device will be unable to initiate the trigger for all SCRs in one direction when moving from injection mode to monitoring mode and vice versa. | During mode transition, no SCR will be handling the line current in one direction. VSLs and device internals may get damaged in case of surge current event. | System will keep working normally. | 3 | Over Current. De-gradation of components. | Usage of over-rated components. | 1 | 3 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | On board SCR gate current measurement. | 2 | 6 | In Bypass Telemetry field 'SCR and Clamp Board Status' will show following: SCR 1 (Output Side): SCRs Off OR SCR 2 (Mid 1 Side): SCRs Off OR SCR 3 (Mid 2 Side): SCRs Off OR SCR 4 (Input Side): SCRs Off | On SmartInterface following Alarm will be raised: If SCR < 100 Permanent Injection Lockout | [9 empty] | 13713
SV104-13714 | 30 V Rail Power Good Circuit - Biasing Resistor | R171, R382 | To provide biasing voltage for the transistor. | Resistor fails open. | Voltage drop across base and emitter not available. No immediate effect. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 1 | Over Current. De-gradation of components. | Usage of over-rated components. | 1 | 1 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | None. | 5 | 5 | None. | None. | [9 empty] | 13714
SV104-13715 |  |  |  | Resistor fails short. | Base and emitter shorted. Overcurrent may cause transistor failure. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 1 | Over Current. De-gradation of components. | Usage of over-rated components. | 1 | 1 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | None. | 5 | 5 | None. | None. | [9 empty] | 13715
SV104-1455 | 30 V Rail Power Good Circuit - Transistor. | Q73, Q75 | 30 V rail check. | Transistor for one rail fails-open. | No immediate effect. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 1 | Over Current. De-gradation of components. | Usage of over-rated components. | 2 | 2 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | None. | 5 | 10 | None. | None. | [9 empty] | -1455
SV104-1456 |  |  |  | Transistors for both rails fail-open. | 30 V rail power good signal not available. Initial pulse and constant current enable circuits will not be functional. Fault-current handling not available in one direction. Device will be unable to initiate the trigger for all SCRs in one direction when moving from injection mode to monitoring mode and vice versa. | During mode transition, no SCR will be handling the line current in one direction. VSLs and device internals may get damaged in case of surge current event. | System will keep working normally. | 3 | Over Current. De-gradation of components. | Usage of over-rated components. | 2 | 6 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | On board SCR gate current measurement. | 2 | 12 | In Bypass Telemetry field 'SCR and Clamp Board Status' will show following: SCR 1 (Output Side): SCRs Off OR SCR 2 (Mid 1 Side): SCRs Off OR SCR 3 (Mid 2 Side): SCRs Off OR SCR 4 (Input Side): SCRs Off | On SmartInterface following Alarm will be raised: If SCR < 100 Permanent Injection Lockout | [9 empty] | -1456
SV104-13716 | 30 V Rail Power Good Circuit - Collector Resistor | R172, R381 | Limiting current to transistor. | Resistor fails open. | Biasing voltage not available to transistor. No immediate effect. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 1 | Over Current. De-gradation of components. | Usage of over-rated components. | 1 | 1 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | None. | 5 | 5 | None. | None. | [9 empty] | 13716
SV104-13717 |  |  |  | Both Resistor fail open. | 30 V rail power good signal not available. Initial pulse and constant current enable circuits will not be functional. Fault-current handling not available in one direction. Device will be unable to initiate the trigger for all SCRs in one direction when moving from injection mode to monitoring mode and vice versa. | During mode transition, no SCR will be handling the line current in one direction. VSLs and device internals may get damaged in case of surge current event. | System will keep working normally. | 3 | Over Current. De-gradation of components. | Usage of over-rated components. | 1 | 3 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | On board SCR gate current measurement. | 2 | 6 | In Bypass Telemetry field 'SCR and Clamp Board Status' will show following: SCR 1 (Output Side): SCRs Off OR SCR 2 (Mid 1 Side): SCRs Off OR SCR 3 (Mid 2 Side): SCRs Off OR SCR 4 (Input Side): SCRs Off | On SmartInterface following Alarm will be raised: If SCR < 100 Permanent Injection Lockout | [9 empty] | 13717
SV104-13718 | 30 V Rail Power Good Circuit - Transistor. | Q74, Q76 | 30 V rail check. | Transistor for one rail fails-open. | No immediate effect. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 1 | Over Current. De-gradation of components. | Usage of over-rated components. | 2 | 2 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | None. | 5 | 10 | None. | None. | [9 empty] | 13718
SV104-13719 |  |  |  | Transistors for both rails fail-open. | 30 V rail power good signal not available. Initial pulse and constant current enable circuits will not be functional. Fault-current handling not available in one direction. Device will be unable to initiate the trigger for all SCRs in one direction when moving from injection mode to monitoring mode and vice versa. | During mode transition, no SCR will be handling the line current in one direction. VSLs and device internals may get damaged in case of surge current event. | System will keep working normally. | 3 | Over Current. De-gradation of components. | Usage of over-rated components. | 2 | 6 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | On board SCR gate current measurement. | 2 | 12 | In Bypass Telemetry field 'SCR and Clamp Board Status' will show following: SCR 1 (Output Side): SCRs Off OR SCR 2 (Mid 1 Side): SCRs Off OR SCR 3 (Mid 2 Side): SCRs Off OR SCR 4 (Input Side): SCRs Off | On SmartInterface following Alarm will be raised: If SCR < 100 Permanent Injection Lockout | [9 empty] | 13719
SV104-13720 | 30 V Rail Power Good Circuit - Schottky Diode | D150, D152 | Ground reverse current protection. | Diodes in one of the rails fail-open. | No immediate effect. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 1 | Over Current. De-gradation of components. | Usage of over-rated components. | 2 | 2 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | None. | 5 | 10 | None. | None. | [9 empty] | 13720
SV104-13721 |  |  |  | Diodes on both rails fail-open. | 30 V rail power good signal not available. Initial pulse and constant current enable circuits will not be functional. Fault-current handling not available in one direction. Device will be unable to initiate the trigger for all SCRs in one direction when moving from injection mode to monitoring mode and vice versa. | During mode transition, no SCR will be handling the line current in one direction. VSLs and device internals may get damaged in case of surge current event. | System will keep working normally. | 3 | Over Current. De-gradation of components. | Usage of over-rated components. | 2 | 6 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | On board SCR gate current measurement. | 2 | 12 | In Bypass Telemetry field 'SCR and Clamp Board Status' will show following: SCR 1 (Output Side): SCRs Off OR SCR 2 (Mid 1 Side): SCRs Off OR SCR 3 (Mid 2 Side): SCRs Off OR SCR 4 (Input Side): SCRs Off | On SmartInterface following Alarm will be raised: If SCR < 100 Permanent Injection Lockout | [9 empty] | 13721
SV104-1457 | 30 V Rail Power Good Circuit - 3.3 V Zener Diode. | D139, D147 | To provide voltage reference. | Diodes in one of the rails fail-open. | No immediate effect. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 1 | Over Current. De-gradation of components. | Usage of over-rated components. | 2 | 1 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | None. | 5 | 10 | None. | None. | [9 empty] | -1457
SV104-1458 |  |  |  | Diodes on both rails fail-open. | 30 V rail power good signal not available. Initial pulse and constant current enable circuits will not be functional. Fault-current handling not available in one direction. Device will be unable to initiate the trigger for all SCRs in one direction when moving from injection mode to monitoring mode and vice versa. | During mode transition, no SCR will be handling the line current in one direction. VSLs and device internals may get damaged in case of surge current event. | System will keep working normally. | 3 | Over Current. De-gradation of components. | Usage of over-rated components. | 2 | 6 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | On board SCR gate current measurement. | 2 | 12 | In Bypass Telemetry field 'SCR and Clamp Board Status' will show following: SCR 1 (Output Side): SCRs Off OR SCR 2 (Mid 1 Side): SCRs Off OR SCR 3 (Mid 2 Side): SCRs Off OR SCR 4 (Input Side): SCRs Off | On SmartInterface following Alarm will be raised: If SCR < 100 Permanent Injection Lockout | [9 empty] | -1458
SV104-1459 | 30 V Rail Power Good Circuit - Reverse Current Protection Diode. | D148, D151 | Reverse current protection. | Diodes in one of the rails fail-open. | No immediate effect. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 1 | Over Current. De-gradation of components. | Usage of over-rated components. | 2 | 2 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | None. | 5 | 10 | None. | None. | [9 empty] | -1459
SV104-1460 |  |  |  | Diodes on both rails fail-open. | 30 V rail power good signal not available. Initial pulse and constant current enable circuits will not be functional. Fault-current handling not available in one direction. Device will be unable to initiate the trigger for all SCRs in one direction when moving from injection mode to monitoring mode and vice versa. | During mode transition, no SCR will be handling the line current in one direction. VSLs and device internals may get damaged in case of surge current event. | System will keep working normally. | 3 | Over Current. De-gradation of components. | Usage of over-rated components. | 2 | 6 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | On board SCR gate current measurement. | 2 | 12 | In Bypass Telemetry field 'SCR and Clamp Board Status' will show following: SCR 1 (Output Side): SCRs Off OR SCR 2 (Mid 1 Side): SCRs Off OR SCR 3 (Mid 2 Side): SCRs Off OR SCR 4 (Input Side): SCRs Off | On SmartInterface following Alarm will be raised: If SCR < 100 Permanent Injection Lockout | [9 empty] | -1460
SV104-1461 | 12 V Power Supply - 12 V Zener Diode. | D138 | To provide 12 V output voltage. | Diode fails-open. | 30 V rail power good signal not available. Initial pulse and constant current enable circuits will not be functional. Fault-current handling not available in one direction. Device will be unable to initiate the trigger for all SCRs in one direction when moving from injection mode to monitoring mode and vice versa. | During mode transition, no SCR will be handling the line current in one direction. VSLs and device internals may get damaged in case of surge current event. | System will keep working normally. | 3 | Over Current. De-gradation of components. | Usage of over-rated components. | 2 | 6 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | On board SCR gate current measurement. | 2 | 12 | In Bypass Telemetry field 'SCR and Clamp Board Status' will show following: SCR 1 (Output Side): SCRs Off OR SCR 2 (Mid 1 Side): SCRs Off OR SCR 3 (Mid 2 Side): SCRs Off OR SCR 4 (Input Side): SCRs Off | On SmartInterface following Alarm will be raised: If SCR < 100 Permanent Injection Lockout | [9 empty] | -1461
SV104-5149 |  |  |  | Diode fails-short. | Overcurrent will cause the diode to eventually fail-open. 30 V rail power good signal not available. Initial pulse and constant current enable circuits will not be functional. Fault-current handling not available in one direction. Device will be unable to initiate the trigger for all SCRs in one direction when moving from injection mode to monitoring mode and vice versa. | During mode transition, no SCR will be handling the line current in one direction. VSLs and device internals may get damaged in case of surge current event. | System will keep working normally. | 3 | Over Current. De-gradation of components. | Usage of over-rated components. | 2 | 6 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | On board SCR gate current measurement. | 2 | 12 | In Bypass Telemetry field 'SCR and Clamp Board Status' will show following: SCR 1 (Output Side): SCRs Off OR SCR 2 (Mid 1 Side): SCRs Off OR SCR 3 (Mid 2 Side): SCRs Off OR SCR 4 (Input Side): SCRs Off | On SmartInterface following Alarm will be raised: If SCR < 100 Permanent Injection Lockout | [9 empty] | -5149
SV104-1462 | 12 V Power Supply - Transistor. | Q71, Q72 | For current amplification. | Transistor fails-open. | 30 V rail power good signal not available. Initial pulse and constant current enable circuits will not be functional. Fault-current handling not available in one direction. Device will be unable to initiate the trigger for all SCRs in one direction when moving from injection mode to monitoring mode and vice versa. | During mode transition, no SCR will be handling the line current in one direction. VSLs and device internals may get damaged in case of surge current event. | System will keep working normally. | 3 | Over Current. De-gradation of components. | Usage of over-rated components. | 2 | 6 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | On board SCR gate current measurement. | 2 | 12 | In Bypass Telemetry field 'SCR and Clamp Board Status' will show following: SCR 1 (Output Side): SCRs Off OR SCR 2 (Mid 1 Side): SCRs Off OR SCR 3 (Mid 2 Side): SCRs Off OR SCR 4 (Input Side): SCRs Off | On SmartInterface following Alarm will be raised: If SCR < 100 Permanent Injection Lockout | [9 empty] | -1462
SV104-5150 |  |  |  | Transistor fails-short. | Overcurrent will cause the transistor to eventually fail-open. 30 V rail power good signal not available. Initial pulse and constant current enable circuits will not be functional. Fault-current handling not available in one direction. Device will be unable to initiate the trigger for all SCRs in one direction when moving from injection mode to monitoring mode and vice versa. | During mode transition, no SCR will be handling the line current in one direction. VSLs and device internals may get damaged in case of surge current event. | System will keep working normally. | 3 | Over Current. De-gradation of components. | Usage of over-rated components. | 2 | 6 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | On board SCR gate current measurement. | 2 | 12 | In Bypass Telemetry field 'SCR and Clamp Board Status' will show following: SCR 1 (Output Side): SCRs Off OR SCR 2 (Mid 1 Side): SCRs Off OR SCR 3 (Mid 2 Side): SCRs Off OR SCR 4 (Input Side): SCRs Off | On SmartInterface following Alarm will be raised: If SCR < 100 Permanent Injection Lockout | [9 empty] | -5150
SV104-1463 | 12 V Power Supply - Resistor Across Output Capacitor. | R174 | To discharge capacitor in case of no supply available. | Resistor fails-open. | Discharging path not available to the output capacitor in case of dead line fault. Fully charged capacitor may damage on board electronics. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 1 | Over Current. De-gradation of components. | Usage of over-rated components. | 1 | 1 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | None. | 5 | 5 | None. | None. | [9 empty] | -1463
SV104-5151 |  |  |  | Resistor fails-short. | Overcurrent will cause the resistor to eventually fail-open. Discharging path not available to the output capacitor in case of dead line fault. Fully charged capacitor may damage on board electronics. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 1 | Over Current. De-gradation of components. | Usage of over-rated components. | 1 | 1 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | None. | 5 | 5 | None. | None. | [9 empty] | -5151
SV104-1464 | 12 V Power Supply - Output Capacitor. | C111 | To suppress noise. | Capacitor fails-open. | No filtration available for noise. Noise can affect performance of onboard electronics | Device can operate in both injection and monitoring mode. | System will keep working normally. | 1 | Over Current. De-gradation of components. | Usage of over-rated components. | 1 | 1 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | None. | 5 | 5 | None. | None. | [9 empty] | -1464
SV104-1465 | Optical Isolators. | U113, U114, U116, U117 | To isolate the signal. | IC failure. (permanently on). | No immediate effect. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 1 | Over Current. De-gradation of components. | Usage of over-rated components. | 2 | 2 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | None. | 5 | 10 | None. | None. | [9 empty] | -1465
SV104-1466 |  |  |  | IC failure. (permanently off). | Continuous back porch and initial pulse current not available to single SCR gate. SCR will be turned off for remaining half-cycles. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 3 | Over Current. De-gradation of components. | 4 parallel SCRs in either direction to ensure loss of a single SCR will not endanger VSLs and other SCRs. | 2 | 6 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | On board SCR gate current measurement. | 3 | 18 | "In Bypass Telemetry field 'SCR and Clamp Board Status' will show following: SCR 1 (Output Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 2 (Mid 1 Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 3 (Mid 2 Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 4 (Input Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) | None. | [9 empty] | -1466
SV104-1467 | Optical Isolators - Reverse Current Protection Diode. | D141, D142, D144, D145 | Reverse current protection. | Diode fails-open. | Continuous back porch and initial pulse current not available to single SCR gate. SCR will be turned off for remaining half-cycles. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 3 | Over Current. De-gradation of components. | 4 parallel SCRs in either direction to ensure loss of a single SCR will not endanger VSLs and other SCRs. | 2 | 6 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | On board SCR gate current measurement. | 3 | 18 | "In Bypass Telemetry field 'SCR and Clamp Board Status' will show following: SCR 1 (Output Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 2 (Mid 1 Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 3 (Mid 2 Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 4 (Input Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) | None. | [9 empty] | -1467
SV104-5152 |  |  |  | Diode fails-short. | Overcurrent will cause the diode to eventually fail-open. Continuous back porch and initial pulse current not available to single SCR gate. SCR will be turned off for remaining half-cycles. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 3 | Over Current. De-gradation of components. | 4 parallel SCRs in either direction to ensure loss of a single SCR will not endanger VSLs and other SCRs. | 2 | 6 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | On board SCR gate current measurement. | 3 | 18 | "In Bypass Telemetry field 'SCR and Clamp Board Status' will show following: SCR 1 (Output Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 2 (Mid 1 Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 3 (Mid 2 Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 4 (Input Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) | None. | [9 empty] | -5152
SV104-1468 | Optical Isolators - Reverse Current Limiting Resistor Output Side. | R383, R391, R392, R395 | Limit the current. | Resistor fails-open. | Continuous back porch and initial pulse current not available to single SCR gate. SCR will be turned off for remaining half-cycles. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 3 | Over Current. De-gradation of components. | 4 parallel SCRs in either direction to ensure loss of a single SCR will not endanger VSLs and other SCRs. | 1 | 3 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | On board SCR gate current measurement. | 3 | 9 | "In Bypass Telemetry field 'SCR and Clamp Board Status' will show following: SCR 1 (Output Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 2 (Mid 1 Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 3 (Mid 2 Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 4 (Input Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) | None. | [9 empty] | -1468
SV104-5153 |  |  |  | Resistor fails-short. | Overcurrent will cause the resistor to fail-open. Continuous back porch and initial pulse current not available to single SCR gate. SCR will be turned off for remaining half-cycles. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 3 | Over Current. De-gradation of components. | 4 parallel SCRs in either direction to ensure loss of a single SCR will not endanger VSLs and other SCRs. | 1 | 3 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | On board SCR gate current measurement. | 3 | 9 | "In Bypass Telemetry field 'SCR and Clamp Board Status' will show following: SCR 1 (Output Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 2 (Mid 1 Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 3 (Mid 2 Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) OR SCR 4 (Input Side): Two SCRs Low Power Fired (1 Clamp) OR Two SCRs Fired (2 Clamps) | None. | [9 empty] | -5153
SV104-1469 | Optical Isolators - Input Side Divider Circuit. | R376, R377, R379, R385, R386, R387, R389, R390 | To control output voltage. | Resistor fails-open. | No immediate effect. Compromised IC protection | Device can operate in both injection and monitoring mode. | System will keep working normally. | 1 | Over Current. De-gradation of components. | Usage of over-rated components. | 1 | 1 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | None. | 5 | 5 | None. | None. | [9 empty] | -1469
SV104-5154 |  |  |  | Resistor fails-short. | Overcurrent will cause the resistor to eventually fail-open. No immediate effect. Compromised IC protection | Device can operate in both injection and monitoring mode. | System will keep working normally. | 1 | Over Current. De-gradation of components. | Usage of over-rated components. | 1 | 1 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | None. | 5 | 5 | None. | None. | [9 empty] | -5154
| SCR Gate Driver Board - Gate Current Feedback | [26 empty] | 0
SV104-1471 | AND Gate IC. | U121, U124 | To implement hardware logic of signals. | Output stuck at permanent high. | Incorrect on-board SCR gate current feedback transmitted to SVMC board. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 2 | Degradation of components. Bad components batch. | Usage of over-rated components. | 2 | 4 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | None. | 5 | 20 | None. | None. | [7 empty] | 0 | Approved | -1471
SV104-1472 |  |  |  | Output stuck at permanent low. | On board SCR gate current feedback not available to SVMC board. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 2 | Degradation of components. Bad components batch. | Usage of over-rated components. | 1 | 2 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | On board SCR gate current measurement. | 1 | 2 | In Bypass Telemetry field 'SCR and Clamp Board Status' will show following: Cable break detected | On SmartInterface following Alarm will be raised: SCR Driver Board Malfunctioning | [9 empty] | -1472
SV104-13722 | Input Capacitors | C347, C348, C349, C350, C351 | To filter glitches in input signal and keeping the signal stable. | Capacitor fails open. | No immediate effect. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 2 | Degradation of components. Bad components batch. | Usage of over-rated components. | 1 | 2 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | None. | 5 | 10 | None. | None. | [9 empty] | 13722
SV104-13723 |  |  |  | Capacitor fails short. | AND gate input shorted to ground. IC output permanently low. On board SCR gate current feedback not available to SVMC board. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 2 | Degradation of components. Bad components batch. | Usage of over-rated components. | 1 | 2 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | On board SCR gate current measurement. | 1 | 2 | In Bypass Telemetry field 'SCR and Clamp Board Status' will show following: Cable break detected | On SmartInterface following Alarm will be raised: SCR Driver Board Malfunctioning | [9 empty] | 13723
SV104-13724 | Voltage Supply Filtering Capacitor | C269, C287, C290, C291, C297, C298 | To filter supply voltage noise. | Capacitor fails-open. | No immediate effect. Noise at output may cause on-board electronics to malfunction. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 1 | Over Voltage De-gradation of components. | Usage of over-rated components. | 1 | 1 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | None. | 5 | 5 | None. | None. | [9 empty] | 13724
SV104-13725 |  |  |  | Capacitor fails-short. | No immediate effect. The respective active device will get stuck at low or high output. Cascading shortage of supply voltage capacitors may cause reduction of single SCR gate current. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 1 | Over Voltage De-gradation of components. | Usage of over-rated components. | 1 | 1 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | None. | 5 | 5 | None. | None. | [9 empty] | 13725
SV104-1473 | 2-To-4 Decoder IC | U122A | To implement hardware logic of signals. | Output stuck at permanent high. | Incorrect on-board SCR gate current feedback transmitted to SVMC board. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 2 | Degradation of components. Bad components batch. | Usage of over-rated components. | 2 | 4 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | None. | 5 | 20 | None. | None. | [9 empty] | -1473
SV104-1474 |  |  |  | Output stuck at permanent low. | On board SCR gate current feedback not available to SVMC board. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 2 | Degradation of components. Bad components batch. | Usage of over-rated components. | 1 | 2 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | On board SCR gate current measurement. | 1 | 2 | In Bypass Telemetry field 'SCR and Clamp Board Status' will show following: Cable break detected | On SmartInterface following Alarm will be raised: SCR Driver Board Malfunctioning | [9 empty] | -1474
SV104-1475 | Multichannel Buffers. | U123 | To provide isolation. | Output stuck at permanent high. | Incorrect on-board SCR gate current feedback transmitted to SVMC board. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 2 | Degradation of components. Bad components batch. | Usage of over-rated components. | 2 | 4 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | None. | 5 | 20 | None. | None. | [9 empty] | -1475
SV104-1476 |  |  |  | Output stuck at permanent low. | On board SCR gate current feedback not available to SVMC board. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 2 | Degradation of components. Bad components batch. | Usage of over-rated components. | 1 | 2 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | On board SCR gate current measurement. | 1 | 2 | In Bypass Telemetry field 'SCR and Clamp Board Status' will show following: Cable break detected | On SmartInterface following Alarm will be raised: SCR Driver Board Malfunctioning | [9 empty] | -1476
SV104-1477 | MOSFET Gate Resistor. | R426, R427, R428, R429 | Limit the instantaneous current. | Resistor fails-open. | Incorrect on-board SCR gate current feedback transmitted to SVMC board. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 2 | Degradation of components. Bad components batch. | Usage of over-rated components. | 1 | 2 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | None. | 5 | 10 | None. | None. | [9 empty] | -1477
SV104-5156 |  |  |  | Resistor fails-short. | Overcurrent will cause the resistor to eventually fail-open. Incorrect on-board SCR gate current feedback transmitted to SVMC board. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 2 | Degradation of components. Bad components batch. | Usage of over-rated components. | 1 | 2 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | None. | 5 | 10 | None. | None. | [9 empty] | -5156
SV104-13726 | MOSFET Drain Capacitors | C250, C253, C256, C268 | To increase/decrease charging and discharging time of 555 timer. | All capacitors fails open. | No charging/discharging path available for 555 timer. No Gate current feedback status is available to SVMC board. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 2 | Degradation of components. Bad components batch. | Usage of over-rated components. | 1 | 2 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | On board SCR gate current measurement. | 1 | 2 | In Bypass Telemetry field 'SCR and Clamp Board Status' will show following: Cable break detected | On SmartInterface following Alarm will be raised: SCR Driver Board Malfunctioning | [9 empty] | 13726
SV104-13727 |  |  |  | One or more capacitors fail open. | The corresponding gate current feedback status frequency will not be available. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 2 | Degradation of components. Bad components batch. | Usage of over-rated components. | 1 | 2 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | None. | 5 | 10 | None. | None. | [9 empty] | 13727
SV104-1478 | 555 Timer IC. | U131 | Provide different frequency signals to communicate on board Gate current feedback. | IC failure | Incorrect on-board SCR gate current feedback transmitted to SVMC board. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 2 | Degradation of components. Bad components batch. | Usage of over-rated components. | 2 | 4 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | None. | 5 | 20 | None. | None. | [9 empty] | -1478
SV104-13728 | 555 Timer Threshold/Discharge Voltage Divider Resistors | R423, R424 | To charge and discharge capacitor. | Resistor fails open. | 555 timer operation is compromised. Gate current feedback not available to SVMC board. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 2 | Degradation of components. Bad components batch. | Usage of over-rated components. | 1 | 2 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | On board SCR gate current measurement. | 1 | 2 | In Bypass Telemetry field 'SCR and Clamp Board Status' will show following: Cable break detected | On SmartInterface following Alarm will be raised: SCR Driver Board Malfunctioning | [9 empty] | 13728
SV104-1479 | Optical Transmitter - Application Circuit - Inductor. | L15 | To suppress noise. | Inductor fails-open. | On board SCR gate current feedback not available to SVMC board. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 2 | Degradation of components. Bad components batch. | Usage of over-rated components. | 1 | 2 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | On board SCR gate current measurement. | 1 | 2 | In Bypass Telemetry field 'SCR and Clamp Board Status' will show following: Cable break detected | On SmartInterface following Alarm will be raised: SCR Driver Board Malfunctioning | [9 empty] | -1479
SV104-5157 |  |  |  | Inductor fails-short. | Reduced noise filtration. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 1 | Degradation of components. Bad components batch. | Usage of over-rated components. | 1 | 1 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | None. | 5 | 5 | None. | None. | [9 empty] | -5157
SV104-1480 | Optical Transmitter. | U126 | Provide optical feedback signal to SVMC board. | Output stuck at permanent high. | On board SCR gate current feedback not available to SVMC board. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 2 | Degradation of components. Bad components batch. | Usage of over-rated components. | 2 | 4 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | On board SCR gate current measurement. | 1 | 4 | In Bypass Telemetry field 'SCR and Clamp Board Status' will show following: Cable break detected | On SmartInterface following Alarm will be raised: SCR Driver Board Malfunctioning | [9 empty] | -1480
SV104-1481 |  |  |  | Output stuck at permanent low. | On board SCR gate current feedback not available to SVMC board. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 2 | Degradation of components. Bad components batch. | Usage of over-rated components. | 1 | 2 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | On board SCR gate current measurement. | 1 | 2 | In Bypass Telemetry field 'SCR and Clamp Board Status' will show following: Cable break detected | On SmartInterface following Alarm will be raised: SCR Driver Board Malfunctioning | [9 empty] | -1481
SV104-13729 | Optical Transmitter Grounding Capacitors | C292,C296 | Prevent reverse current/ripples. | Capacitor fails short. | 5V Supply gets shorted to ground. No local power to the affected SCR gate driver board. Fault-current handling not available in one direction. Device will be unable to initiate the trigger for all SCRs in one direction when moving from injection mode to monitoring mode and vice-versa. | During mode transition, no SCR will be handling the line current in one direction. IGBTs may get damaged in case of surge current event, if loss of SCRs occurs in injection mode. Device's default behavior will be to disallow injection mode operation. The device is capable of injection, however, and end user may request to override this protection. | Affected device and its associated group of devices will transit to monitoring mode. System will keep working with reduced injection capability. | 4 | Over Voltage De-gradation of components. | Usage of over-rated components. | 1 | 4 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | On board SCR gate current measurement. | 1 | 4 | In Bypass Telemetry field 'SCR and Clamp Board Status' will show following: Cable break detected | On SmartInterface following Alarm will be raised: SCR Driver Board Malfunctioning | [9 empty] | 13729
SV104-13730 |  |  |  | Capacitor fails open. | No immediate effect. There maybe a floating point voltage that can cause a false signal. On board SCR gate current feedback to SVMC board might be compromised. |  | System will keep working normally. | 1 | Over Voltage De-gradation of components. | Usage of over-rated components. | 1 | 1 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | None. | 5 | 5 | None. | None. | [9 empty] | 13730
SV104-13731 | Optical Transmitter Data In Pull-down Resistor | R425 | Keeping the normal input at low. | Resistor fails short. | No input voltages available at the pin. Transmitter will not be able to send any signal. On board SCR gate current feedback not available to SVMC board. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 1 | Over Voltage De-gradation of components. | Usage of over-rated components. | 1 | 1 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | On board SCR gate current measurement. | 1 | 1 | In Bypass Telemetry field 'SCR and Clamp Board Status' will show following: Cable break detected | On SmartInterface following Alarm will be raised: SCR Driver Board Malfunctioning | [9 empty] | 13731
SV104-13732 |  |  |  | Resistor fails open. | No immediate effect. There maybe a floating point voltage that can cause a false signal. On board SCR gate current feedback to SVMC board might be compromised. |  | System will keep working normally. | 1 | Over Voltage De-gradation of components. | Usage of over-rated components. | 1 | 1 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | None. | 5 | 5 | None. | None. | [9 empty] | 13732
SV104-13733 | Buck Regulator Circuit - Input Inductor | L25 | Switching supply harmonics suppression. | Inductor fails-open. | Loss of single 5 V supply. Redundant 5 V supply will provide power to on-board electronics | Device's default behavior will be to disallow injection mode operation. The device is capable of injection, however, and end user may request to override this protection. | System will keep working normally. | 3 | Over Current. De-gradation of components. | Usage of over-rated components. | 1 | 3 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | None. | 5 | 15 | None. | None. | [9 empty] | 13733
SV104-13734 |  |  |  | Inductor fails-short. | Noise can affect performance of onboard surge detection circuit for positive half cycle. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 1 | Over Current. De-gradation of components. | Usage of over-rated components. | 1 | 1 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | None. | 5 | 5 | None. | None. | [9 empty] | 13734
SV104-13735 | Buck Regulator Circuit - Input Capacitors | C363, C364 | To filter out noise. To suppress input spikes. | Capacitor fails-open. | Noise can affect performance of onboard surge detection circuit for positive half cycle. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 1 | Over Current. De-gradation of components. | Usage of over-rated components. | 1 | 1 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | None. | 5 | 5 | None. | None. | [9 empty] | 13735
SV104-13736 |  |  |  | Capacitor fails-short. | Both 30 V rails will be shorted to ground. No power to the affected SCR gate driver board. Fault-current handling not available in one direction. Device will be unable to initiate the trigger for all SCRs in one direction when moving from injection mode to monitoring mode and vice versa. | During mode transition, no SCR will be handling the line current in one direction. IGBTs may get damaged in case of surge current event, if loss of SCRs occurs in injection mode. Device's default behavior will be to disallow injection mode operation. The device is capable of injection, however, and end user may request to override this protection. | System will keep working normally. | 4 | Over Current. De-gradation of components. | Usage of over-rated components. | 1 | 4 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | On board SCR gate current measurement. | 1 | 4 | In Bypass Telemetry field 'SCR and Clamp Board Status' will show following: Cable break detected | On SmartInterface following Alarm will be raised: SCR Driver Board Malfunctioning | [9 empty] | 13736
SV104-13737 | Buck Regulator Circuit - Voltage Divider Resistors | R494, R497, R498 | Adjust under voltage lockout for regulator IC. | One of the series resistor fails-open. | Less than 1.2 V at enable pin of regulator IC will disable the regulator. Redundant 5 V supply will provide power to onboard electronics | Device can operate in both injection and monitoring mode. | System will keep working normally. | 3 | Over Current. De-gradation of components. | Usage of over-rated components. | 1 | 3 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | None. | 5 | 15 | None. | None. | [9 empty] | 13737
SV104-13738 |  |  |  | High-side resistor fails-short. | Overcurrent will cause the resistor to eventually fail-open. Less than 1.2 V at enable pin of regulator IC will disable the regulator. Redundant 5 V supply will provide power to onboard electronics | Device can operate in both injection and monitoring mode. | System will keep working normally. | 3 | Over Current. De-gradation of components. | Usage of over-rated components. | 1 | 3 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | None. | 5 | 15 | None. | None. | [9 empty] | 13738
SV104-13739 |  |  |  | Low-side resistor fails-short. | Less than 1.2 V at enable pin of regulator IC will disable the regulator. Redundant 5 V supply will provide power to onboard electronics | Device can operate in both injection and monitoring mode. | System will keep working normally. | 3 | Over Current. De-gradation of components. | Usage of over-rated components. | 1 | 3 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | None. | 5 | 15 | None. | None. | [9 empty] | 13739
SV104-13740 | Buck Regulator Circuit - 12V Zener Diode | D154 | Overvoltage protection for regulator IC. | Diode fails-open. | Overvoltage protection will be compromised, however higher voltages will be clamped internally with a 5.8 V Zener diode. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 2 | Over Voltage De-gradation of components. | Usage of over-rated components. | 2 | 4 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | None. | 5 | 20 | None. | None. | [9 empty] | 13740
SV104-13741 |  |  |  | Diode fails-short. | 5 V supply will be lost. Redundant 5 V supply will provide power to onboard electronics | Device can operate in both injection and monitoring mode. | System will keep working normally. | 3 | Over Current. De-gradation of components. | Usage of over-rated components. | 1 | 3 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | None. | 5 | 15 | None. | None. | [9 empty] | 13741
SV104-13742 | Buck Regulator Circuit - Reset Pin Resistor | R499 | To set switching frequency. | Resistor fails-open | 5 V supply will be lost. Redundant 5 V supply will provide power to onboard electronics | Device can operate in both injection and monitoring mode. | System will keep working normally. | 3 | De-gradation of components. | Usage of over-rated components. | 1 | 3 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | None. | 5 | 15 | None. | None. | [9 empty] | 13742
SV104-13743 |  |  |  | Resistor fails-short. | 5 V supply will be lost. Redundant 5 V supply will provide power to onboard electronics | Device can operate in both injection and monitoring mode. | System will keep working normally. | 3 | De-gradation of components. | Usage of over-rated components. | 1 | 3 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | None. | 5 | 15 | None. | None. | [9 empty] | 13743
SV104-13744 | Buck Regulator Circuit - Catch Diode | D153 | Maintain voltage at output. | Diode fails-open. | Voltage maintenance at regulator's output will be affected if heavily loaded. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 2 | Overvoltage. De-gradation of components. | Usage of over-rated components. | 2 | 4 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | None. | 5 | 20 | None. | None. | [9 empty] | 13744
SV104-13745 |  |  |  | Diode fails-short. | Bootstrap capacitor will be shorted to ground. Loss of single 5 V supply. Redundant 5 V supply will provide power to onboard electronics | Device can operate in both injection and monitoring mode. | System will keep working normally. | 3 | Overvoltage. De-gradation of components. | Usage of over-rated components. | 1 | 3 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | None. | 5 | 15 | None. | None. | [9 empty] | 13745
SV104-13746 | Buck Regulator Circuit - Bootstrap Capacitor | C358 | To supply switching currents to the high and low side gate drivers. | Capacitor fails-open. | Loss of single 5 V supply. Redundant 5 V supply will provide power to onboard electronics | Device can operate in both injection and monitoring mode. | System will keep working normally. | 3 | Overvoltage. De-gradation of components. | Usage of over-rated components. | 1 | 3 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | None. | 5 | 15 | None. | None. | [9 empty] | 13746
SV104-13747 |  |  |  | Capacitor fails-short. | Loss of single 5 V supply. Redundant 5 V supply will provide power to onboard electronics | Device can operate in both injection and monitoring mode. | System will keep working normally. | 3 | Overvoltage. De-gradation of components. | Usage of over-rated components. | 1 | 3 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | None. | 5 | 15 | None. | None. | [9 empty] | 13747
SV104-13748 | Buck Regulator Circuit - Output Inductor | L24 | To maintain current flow during off state of the supply. | Inductor fails-open. | Loss of single 5 V supply. Redundant 5 V supply will provide power to onboard electronics | Device can operate in both injection and monitoring mode. | System will keep working normally. | 3 | Overvoltage. De-gradation of components. | Usage of over-rated components. | 1 | 3 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | None. | 5 | 15 | None. | None. | [9 empty] | 13748
SV104-13749 |  |  |  | Inductor fails-short. | Unstable operating of the switch mode power supply will happen. On-board electronics might get damaged due to unstable operation. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 1 | Overvoltage. De-gradation of components. | Usage of over-rated components. | 1 | 1 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | None. | 5 | 5 | None. | None. | [9 empty] | 13749
SV104-13750 | Buck Regulator Circuit - Compensation RC Circuit | R495, C365, C366 | To filter out noise. | Capacitor (C365) fails-open. | No filtration available for noise. Noise can affect performance of onboard surge detection circuit for positive half cycle. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 1 | Over Current. De-gradation of components. | Usage of over-rated components. | 1 | 1 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | None. | 5 | 5 | None. | None. | [9 empty] | 13750
SV104-13751 |  |  |  | Capacitor (C365) fails-short. | Loss of single 5 V supply. Redundant 5 V supply will provide power to onboard electronics | Device can operate in both injection and monitoring mode. | System will keep working normally. | 3 | Over Current. De-gradation of components. | Usage of over-rated components. | 1 | 3 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | None. | 5 | 15 | None. | None. | [9 empty] | 13751
SV104-13752 |  |  |  | Capacitor (C366) fails-open. | No filtration available for noise. Noise can affect performance of onboard surge detection circuit for positive half cycle. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 1 | Over Current. De-gradation of components. | Usage of over-rated components. | 1 | 1 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | None. | 5 | 5 | None. | None. | [9 empty] | 13752
SV104-13753 |  |  |  | Capacitor (C366) fails-short.. | Overcurrent will cause the capacitor to eventually fail-open. No filtration available for noise. Performance will be effected. Noise can affect performance of onboard surge detection circuit for positive half cycle. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 1 | Over Current. De-gradation of components. | Usage of over-rated components. | 1 | 1 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | None. | 5 | 5 | None. | None. | [9 empty] | 13753
SV104-13754 |  |  |  | Resistor fails-open. | No filtration available for noise. Noise can affect performance of onboard surge detection circuit for positive half cycle. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 1 | Over Current. De-gradation of components. | Usage of over-rated components. | 1 | 1 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | None. | 5 | 5 | None. | None. | [9 empty] | 13754
SV104-13755 |  |  |  | Resistor fails-short. | Overcurrent will cause the resistor to eventually fail-open. No filtration available for noise. Noise can affect performance of onboard surge detection circuit for positive half cycle. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 1 | Over Current. De-gradation of components. | Usage of over-rated components. | 1 | 1 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | None. | 5 | 5 | None. | None. | [9 empty] | 13755
SV104-13756 | Buck Regulator Circuit - Feedback Resistors | R493, R496 | Provide output voltage feedback to the switcher to maintain output voltage accuracy. | High-side resistor fails-open. | Input voltage will be replicated at regulator output. Over Voltage at the output may damage the ideal diodes of both 5V and redundant supply and on board electronics may get damaged. Loss of both 5 V power supplies SCR driver board will not be functional. Fault-current handling will not be available in one direction. | During mode transition, no SCR will be handling the line current in one direction. IGBTs may get damaged in case of surge current event, if loss of SCRs occurs in injection mode. Device's default behavior will be to disallow injection mode operation. The device is capable of injection, however, and end user may request to override this protection. | System will keep working normally. | 4 | Over Current. De-gradation of components. | Usage of over-rated components. | 1 | 4 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | On board SCR gate current measurement. | 1 | 4 | In Bypass Telemetry field 'SCR and Clamp Board Status' will show following: Cable break detected | On SmartInterface following Alarm will be raised: SCR Driver Board Malfunctioning | [9 empty] | 13756
SV104-13757 |  |  |  | High-side resistor fails-short.. | Loss of single 5 V supply. Redundant 5 V supply will provide power to onboard electronics | Device can operate in both injection and monitoring mode. | System will keep working normally. | 3 | Overvoltage. De-gradation of components. | Usage of over-rated components. | 1 | 3 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | None. | 5 | 15 | None. | None. | [9 empty] | 13757
SV104-13758 |  |  |  | Low-side resistor fails-short. | Input voltage will be replicated at regulator output. Over Voltage at the output may damage the ideal diodes of both 5V and redundant supply and on board electronics may get damaged. Loss of both 5 V power supplies SCR driver board will not be functional. Fault-current handling will not be available in one direction. | During mode transition, no SCR will be handling the line current in one direction. IGBTs may get damaged in case of surge current event, if loss of SCRs occurs in injection mode. Device's default behavior will be to disallow injection mode operation. The device is capable of injection, however, and end user may request to override this protection. | System will keep working normally. | 4 | Over Current. De-gradation of components. | Usage of over-rated components. | 1 | 4 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | On board SCR gate current measurement. | 1 | 4 | In Bypass Telemetry field 'SCR and Clamp Board Status' will show following: Cable break detected | On SmartInterface following Alarm will be raised: SCR Driver Board Malfunctioning | [9 empty] | 13758
SV104-13759 | Buck Regulator Circuit - Output Capacitors | C359, C360, C361, C362 | Filter inductor ripple currents Supply the increased load current until the regulator responds to the load step. | One of the output capacitors fail-open. | Reduced filtering capacity against output inductor's ripple currents. Capability to provide increased load current may be affected until the regulator responds to load step. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 1 | Overvoltage. De-gradation of components. | Usage of over-rated components. | 1 | 1 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | None. | 5 | 5 | None. | None. | [9 empty] | 13759
SV104-13760 |  |  |  | Multiple output capacitors fail-open. | No filtration available for noise. Noise can affect performance of onboard surge detection circuit for positive half cycle. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 1 | Over Current. De-gradation of components. | Usage of over-rated components. | 1 | 1 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | None. | 5 | 5 | None. | None. | [9 empty] | 13760
SV104-13761 | Buck Regulator Circuit -Buck Regulator IC | U145 | Step down 30V to 5V. | IC failure. | Loss of single 5 V supply. Redundant 5 V supply will provide power to onboard electronics | Device can operate in both injection and monitoring mode. | System will keep working normally. | 3 | Over Current. De-gradation of components. | Usage of over-rated components. | 2 | 6 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | None. | 5 | 30 | None. | None. | [9 empty] | 13761
SV104-13762 | Buck Regulator Circuit - Ideal Diode | U146 | Reverse Current Protection. | IC failure. (Permanent low). | Loss of single 5 V supply. Redundant 5 V supply will provide power to onboard electronics | Device can operate in both injection and monitoring mode. | System will keep working normally. | 3 | Over Current. De-gradation of components. | Usage of over-rated components. | 2 | 6 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | None. | 5 | 30 | None. | None. | [9 empty] | 13762
SV104-13763 | Buck Regulator Circuit - 5V Output Capacitor | C367 | Filter inductor ripple currents Supply the increased load current until the regulator responds to the load step. | One of the output capacitors fail-open. | Reduced filtering capacity against output inductor's ripple currents. Capability to provide increased load current may be affected until the regulator responds to load step. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 1 | Overvoltage. De-gradation of components. | Usage of over-rated components. | 1 | 1 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | None. | 5 | 5 | None. | None. | [9 empty] | 13763
SV104-13764 |  |  |  | Multiple output capacitors fail-open. | No filtration available for noise. Noise can affect performance of onboard surge detection circuit for positive half cycle. | Device can operate in both injection and monitoring mode. | System will keep working normally. | 1 | Over Current. De-gradation of components. | Usage of over-rated components. | 1 | 1 | Functional Testing. Thermal and Relative Humidity Testing. Condensed Humidity Testing. EFT Testing. Vibration Testing. ATM Testing. MVAr Testing. Pre-Closure Testing. EOL Testing. | None. | 5 | 5 | None. | None. | [9 empty] | 13764
0
0

## Data Validation (hidden)
Status
Approved
Review Pending
Reviewed by QA